F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfil the BAT_AEL values of the LCP BREF note.
G. Warm start is starting with a glowing bed and a warm deaerator.
H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09b Wood Pellets extract. plant
Technology |  | Biomass CHP - extraction - wood pellets - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 356.4 | 357.6 | 358.7 | 358.4 | 347.3 | 359.4 | 351.7 | 364.4 | A
| Electrical efficiency (net, annual average) [] | 42.3% | 42.5% | 42.6% | 42.6% | 41.2% | 42.7% | 41.8% | 43.3% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 44.5% | 44.7% | 44.8% | 44.8% | 43.4% | 44.9% | 44% | 45.5% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.59 | 0.59 | 0.59 | 0.52 | 0.57 | 0.52 | 0.59 | 0.53
| Cv coefficient (50°C/100°C) | 0.17 | 0.17 | 0.17 | 0.15 | 0.17 | 0.15 | 0.17 | 0.15 | I
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 5 | 1 | 1 | 1 |  | 1
| Space requirement [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring) [] | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% |  | [1, 2]
| NOX [g/GJ_i] | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | [C, F] | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | [1, 2]
| N2O [g/GJ_i] | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 |  | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | [1, 2]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.3607 | 2.2863 | 2.1693 | 2.0204 | 2.0523 | 2.7541 | 1.9141 | 2.9562 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_e] | 1.4249 | 1.3824 | 1.3079 | 1.2335 | 1.2335 | 1.6801 | 1.1484 | 1.8077 | K
| Nominal investment (installation) [MEUR/MW_e] | 0.93577 | 0.9145 | 0.86133 | 0.7869 | 0.8188 | 1.0634 | 0.75499 | 1.1484 | K
| Variable O&M (*total) [EUR/MWh_e] | 1.1697 | 1.1697 | 1.1697 | 1.1697 | 1.276 | 1.1697 | 1.276 | 1.1697 | L
| Fixed O&M (*total) [EUR/MW_e/y] | 60612.2449 | 58485.4995 | 55295.3813 | 52105.2632 | 54232.0086 | 66992.4812 | 48915.145 | 66992.4812 | 0
Technology-specific data
| Nominal investment (*total) [MEUR/MW_i] | 1.0527 | 1.0208 | 0.9783 | 0.90387 | 0.89323 | 1.2335 | 0.84006 | 1.3398 | [J, K] | 1
| Nominal investment (equipment) [MEUR/MW_i] | 0.62739 | 0.61676 | 0.58485 | 0.55295 | 0.54232 | 0.75499 | 0.51042 | 0.8188 | K
| Nominal investment (installation) [MEUR/MW_i] | 0.41472 | 0.40408 | 0.38281 | 0.35091 | 0.35091 | 0.47852 | 0.32965 | 0.52105 | K
| Variable O&M (*total) [EUR/MWh_i] | 0.54232 | 0.54232 | 0.54232 | 0.54232 | 0.54232 | 0.54232 | 0.54232 | 0.54232 | L
| Fixed O&M (*total) [EUR/MW_i/y] | 26796.9925 | 26158.9689 | 24989.2589 | 23287.8625 | 23606.8743 | 30093.4479 | 21267.4544 | 30412.4597
| Fuel storage specific cost in excess of 2 days [MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
Steam reheat | bar: ctrl to -
| Flue gas condensation | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | M
| Combustion air humidification | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | M
| Additional heat potential with heat pumps (of thermal input) [] | ctrl: 3.6%; upper: 3.6%; upper: 3.6%; -: C; -: 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent extraction steam turbine with steam reheat.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield additional 6% (of thermal input) when operated with combustion air humidification and assuming 50 °C DH return temperature. DH water may be heated in two (or more) stages, first stage being direct condensation (at hardly any drop in electricity output), second stage extraction steam with drop in electricity output, cf. the listed Cv-value. For the 2050 estimate flue gas condensation has been included to super-optimize and show the order of advantage is a reduction of the Cv of 0.02 as resulting average for maximum heat output including condensation.
D. This is given by grid code (Energinet.dk)
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. This plant is equipped with a Tail-end SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G. Warm start is starting with the steam system being pressurized.
H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value may vary according to the optimisation of the plant. A modest value representing a choice with current power/heat prices is shown.
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 10 Stirling
Technology |  | Stirling engine - back pressure - biomass - medium
year |  | 2015 | 2020 | 2030 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.04 | 0.04 |  |  |  | 1
| Electrical efficiency (net, name plate) [] | 20% | 22% |  |  | A | 1
| Forced outage [] | 4% | 3% |  |  |  | 1
| Planned outage [weeks per year] | 3 | 2 |  |  |  | 1
| Technical lifetime [years] | 15 | 15 |  |  |  | 1
| Construction time [years] | 0.4 | 0.3 |  |  | B | 1
Regulation ability
| Cold start-up time [hours] | 1 | 1 |  |  |  | 1
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% |  |  |  | 1
| NOX [ppm] | 130 | 100 |  |  |  | 1
| CH4 [ppm] | 0 | 0 |  |  |  | 1
| N2O [ppm] | 0 | 0 |  |  |  | 1
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 5.3169 | 4.0408 | 0 | 0 | [C, E] | 1
| Variable O&M (*total) [EUR/MWh_e] | 27.6477 | 22.3308 | 0 | 0 | [D, E] | 1
| Fixed O&M (*total) [EUR/MW_e/y] | 34027.927 | 34027.927 | 0 | 0 | [D, E] | 1
Technology-specific data
| Generating capacity for one unit [MW_h] | 0.12 | 0.12 |  |  |  | 1
Notes:
A. The efficiency of the gasifier is 97%, while the total efficiency for the whole system is 90% (2020).
B. The plants may be delivered as pre-assembled container solutions reducing construction times on site to a couple of weeks.
C. Complete plant, including gasifier, combustion chambers, engines, control system, piping, and instrumentation.
D. O&M for the Stirling engine itself is (2010) around 16 EUR/MWh, while the remianing O&M costs are for biomass feeding, gasification, heat exchangers etc.
E. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Stirling DK, December 2009

## 11 SOFC-CHP
Technology |  | Solid oxide fuel cell - back pressure - biogas - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.25 | 2.5 | 10 | 20 |  |  |  |  | A | [3, *, *, *]
| Electrical efficiency (net, annual average) [] | 56% | 58% | 60% | 60% | 52% | 60% | 56% | 62% | B | [3, *, *, *]
| Electrical efficiency (net, name plate) [] | ctrl: 56%; ctrl: 58%; ctrl: 60%; ctrl: 60%
| Cb coefficient (50°C/100°C) | ctrl: 1.67; ctrl: 1.61; ctrl: 1.61; -: [C, L]; -: [, *, *, *]
Cv coefficient (50°C/100°C)
Forced outage []
Planned outage [weeks per year]
| Technical lifetime [years] | 15 | 20 | 20 | 20 |  |  |  |  | D | [6, 6, *, *]
Construction time [years] | bar: ctrl to ctrl
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | ctrl: 70%; ctrl: 70%; ctrl: 70%; ctrl: 70%
| Warm start-up time [hours] | ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; -: E
| Cold start-up time [hours] | 25 | 25 | 25 | 25 |  |  |  |  | E | [*, *, *, *]
Environment
| SO2 (degree of desulphuring) [] | ctrl: 100%; ctrl: 100%; ctrl: 100%; ctrl: 100%; -: 3
| NOX [g/GJ_i] | ctrl: 1.3; ctrl: 1.4; ctrl: 1.5; ctrl: 1.6; -: 3
| CH4 [g/GJ_i] | 1.25 | 1.25 | 1.25 | 1.25 |  |  |  |  | F | 7
N2O [g/GJ_i] | bar: - to -
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 8.826 | 3.5091 | 2.1267 | 0.8507 | 2.8711 | 6.1676 | 0.42535 | 1.3824 | [G, H, I, J] | [8, 13]
| Nominal investment (equipment) [MEUR/MW_e] | 7.0608 | 2.4564 | 1.276 | 0.48915 | 0 | 0 | 0 | 0 | G
| Nominal investment (installation) [MEUR/MW_e] | 1.7652 | 1.0527 | 0.8507 | 0.36155 | 0 | 0 | 0 | 0 | G
| Variable O&M (*total) [EUR/MWh_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [EUR/MW_e/y] | 441299.678 | 175456.4985 | 106337.2718 | 42534.9087 | 143555.3169 | 308378.0882 | 21267.4544 | 69119.2267 | K | 8
| Startup cost [EUR/MW_e/startup] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
Notes:
A. Installed systems consist of modules of app. 200 kWel power, these modules can be clustered into larger units. Today, often up to app. 2 MWel power and upwards. [5,8]
B. The electrical efficiency (based on the lower heating value, LHV) of Bloom Energy's systems decreases from an initial value of 60 % to 52 % by the end-of life for the stacks. This gives an average electrical efficiency of 56 % for the life-time of a stack. Uncertainties represent the aforementioned interval.
C. No CHP-systems in this power range are available, therefore, Bloom Energy ES-5710 unit has been chosen as the reference system. This system is a power producing system and does not take the produced heat into account. . The produced heat can be used as thermal storage, hot water production, heating or for feed in to the distributed heating system. High total efficiencies can be expected as the systems are compact and with a small surface area, leading to low heat losses and thereby high total system efficiency. Thus it is not unrealistic to assume a total efficiency above 90 % (thermal efficiency > 35 %) for this type of system.
D. Values correspond to the durability for the whole plant; the stack may be exchanged several times during the life time of the plant.
E. Start up from outdoor temperature or room temperature takes rather long time, this is mainly due to the large amount of ceramic material which require slow heating ramps. If the system is at operating temperature the stack can be started up quickly, assuming that gases are supplied and help systems are active. Also shut down can be performed quickly, not counting in the time required to cool the system.
F. Value for SOFC microCHP systems used here, since SOFC-CHP's has the same operating principle.
G. A bloom unit costs approximately 6600 euro per kWel. To this must the installation costs be added, which of course depends on the location and the size of the unit. Additional costs are also to cover for necessary modifications of the system, e.g. implementation of hot water storage and subsystems for exporting the heat from the unit to surrounding buildings or distributed heating grid.
H. Start up from outdoor temperature or room temperature takes rather long time, this is mainly due to the large amount of ceramic material which require slow heating ramps. If the system is at operating temperature the stack can be started up quickly, assuming that gases are supplied and help systems are active. Also shut down can be performed quickly, not counting in the time required to cool the system.
I. The best estimates for nominal investments in 2020, 2030 and 2050 are estimated from [9]. In 2020 an annual production of 50 units is assumed, in 2030 a yearly production of 250 units is assumed, and in 2050 a production of 4000 units per year is assumed.
J. Estimation of uncertainties for investment costs are estimated from [9] with an annual production of 10/150 units in 2020 and 1000/10000 units in 2050
K. Fixed O&M costs are estimated as 5% of the investment cost.
L. The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
M. An asterisk (*) in the reference indicate high uncertainty or "guesstimate", where more certain data where not available
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. BloomEnergy, www.bloomenergy.com, 2014-11-11
2. https://www.mhps.com/en/technology/index.html, 2014-11-14
3. BloomEnergy, Product datasheet: ES-5710 Energy Saver, November 2014: http://c0688662.cdn.cloudfiles.rackspacecloud.com/downloads_pdf_Bloomenergy_DataSheet_ES-5710.pdf
4. BloomEnergy, Product datasheet: ES-5700 Energy Saver, November 2014: http://c0688662.cdn.cloudfiles.rackspacecloud.com/downloads_pdf_Bloomenergy_DataSheet_ES-5700.pdf
5. Iskov H., Rasmussen N.B., "Update of technology data for energy plants: Fuel cells, electrolysis and technologies for bio-SNG", Danish gas Technology centre, 2013.
6. Fuel Cell and Hydrogen Joint Undertaking: "Multi - Annual Work Plan 2014-2020", adopted 2014-06-30
7. http://www.asue.de, 2014-11-17
8. BloomEnergy Server, http://en.wikipedia.org/wiki/Bloom_Energy_Server, 02-02
13. Chick, LA; Gotthold, DW; Weimar, MR; Whyatt, GA, Cost Study for Manufacturing of Solid Oxide Fuel Cell Power Systems, 2013, Pacific Northwest National Laboratory prepared for the U.S. Department of Energy.

## 12 LT-PEMFC CHP
Technology |  | Low temp PEM fuel cell - back pressure - hydrogen - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 0.05; ctrl: 0.1; ctrl: 1; ctrl: 2; -: 5
| Electrical efficiency (net, annual average) [] | 45% | 50% | 50% | 50% | 45% | 52% | 46% | 53% | A | [3, 5]
| Electrical efficiency (net, name plate) [] | ctrl: 45%; ctrl: 50%; ctrl: 50%; ctrl: 50%; -: 5
| Cb coefficient (50°C/100°C) | ctrl: 1.25; ctrl: 1.25; ctrl: 1.25; -: D
Cv coefficient (50°C/100°C)
| Forced outage [] | ctrl: 0.1%; ctrl: 0.1%; ctrl: 0.1%; ctrl: 0.1%
| Planned outage [weeks per year] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1
| Technical lifetime [years] | ctrl: 10; ctrl: 10; ctrl: 10; ctrl: 10; -: 5
Construction time [years] | bar: ctrl to ctrl
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | ctrl: 50%; ctrl: 25%; ctrl: 2.5%; ctrl: 1.25%
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | ctrl: 10%; ctrl: 10%; ctrl: 10%; ctrl: 10%
| Warm start-up time [hours] | ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01
Cold start-up time [hours]
Environment
| SO2 (degree of desulphuring) [] | ctrl: 100%; ctrl: 100%; ctrl: 100%; ctrl: 100%
| NOX [g/GJ_i] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| CH4 [g/GJ_i] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| N2O [g/GJ_i] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.0204 | 1.3824 | 1.1697 | 0.8507 | 1.1697 | 1.7014 | 0.53169 | 0.95704 | B | [3, 4]
| Nominal investment (equipment) [MEUR/MW_e] | 1.7014 | 1.0634 | 0.8507 | 0.63802 | 0 | 0 | 0 | 0 | 0 | 4
| Nominal investment (installation) [MEUR/MW_e] | 0.31901 | 0.31901 | 0.31901 | 0.21267 | 0 | 0 | 0 | 0 | 0 | 4
| Variable O&M (*total) [EUR/MWh_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [EUR/MW_e/y] | 101020.4082 | 69119.2267 | 58485.4995 | 42534.9087 | 0 | 0 | 0 | 0 | C
Technology-specific data
| Minimum load efficiency [] | ctrl: 30%; ctrl: 35%; ctrl: 35%; ctrl: 35%; -: 5
Notes:
A. Uncertainties for efficiency based on [2]
B. Estimation of uncertainties for nominal investment costs based on [2]
C. Fixed O&M costs are estimated to 5% of the investment cost based on [2]
D. The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
E. An asterisk (*) in the reference indicate high uncertainty or "guesstimate", where more certain data where not available.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. International Energy Agency, 2015, Technology Roadmap - Hydrogen and Fuel Cells.
4. Ea Energy Analyses et al. 2016, Technology Data for Hydrogen Technologies.
5. Practical data and expert opinion from Dantherm Power

## 20 Onshore turbines
Technology |  | Onshore wind turbine, utility - renewable power - wind - large
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 3.1 | 4.2 | 5 | 5.5 | 6 | 2 | 6 | 1.5 | 8 | A1 | 3
| Forced outage [] | 3% | 2.5% | 2% | 1.8% | 1.5% | 1% | 5% | 1% | 5% | B | 4
| Planned outage [weeks per year] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 | C | 4
| Technical lifetime [years] | 25 | 27 | 30 | 30 | 30 | 25 | 35 | 25 | 40 | D | 14
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 3 | 1 | 3 | E | 4
Space requirement [1000 m2/MW_e] | bar: -
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.4143 | 1.191 | 1.1059 | 1.0421 | 1.0208 | 0.8188 | 1.2335 | 0.8507 | 1.2654 |  | [16, 2, 4]
| Nominal investment (equipment) [MEUR/MW_e] | 0.9464 | 0.75499 | 0.68056 | 0.62739 | 0.61676 | 0.60612 | 0.9145 | 0.48915 | 0.73373 |  | 25
| Nominal investment (installation) [MEUR/MW_e] | 0.1276 | 0.095704 | 0.08507 | 0.08507 | 0.074436 | 0.074436 | 0.11697 | 0.063802 | 0.095704 | M | 25
| Nominal investment (decommissioning of existing turbines) [MEUR/MW_e] | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.031901 | 0.042535 | 0.031901 | 0.042535 |  | 25
| Nominal investment (grid connection) [MEUR/MW_e] | 0.063802 | 0.053169 | 0.053169 | 0.053169 | 0.053169 | 0.042535 | 0.063802 | 0.042535 | 0.063802 |  | 25
| Nominal investment (other, i.e. compensation of neighbours) [MEUR/MW_e] | 0.13824 | 0.14887 | 0.14887 | 0.14887 | 0.14887 | 0.11697 | 0.18077 | 0.11697 | 0.18077 | I | [25, 26]
| Nominal investment (land rent) [MEUR/MW_e] | 0.095704 | 0.095704 | 0.095704 | 0.095704 | 0.095704 | 0.074436 | 0.10634 | 0.074436 | 0.10634 |  | 25
| Variable O&M (*total) [EUR/MWh_e] | 2.9774 | 1.5951 | 1.4356 | 1.3186 | 1.2973 | 1.276 | 1.9141 | 1.0315 | 1.5525
| Fixed O&M (*total) [EUR/MW_e/y] | 27222.3416 | 14887.2181 | 13398.4962 | 12326.6165 | 12058.6466 | 11909.7744 | 17864.6617 | 9646.9173 | 14470.3759 | I | [25, 26]
Technology-specific data
| Availability [] | 96.7% | 97.2% | 97.7% | 97.7% | 98.2% | 98.9% | 94.5% | 98.9% | 94.5%
| Hub height [m] | 85 | 85 | 100 | 105 | 110 | 85 | 120 | 85 | 150 |  | [4, 26]
| Rotor diameter [m] | 106 | 130 | 145 | 155 | 165 | 90 | 130 | 100 | 150 | K | [4, 26]
| Specific power [W_e/m2] | 351.29 | 316.43 | 302.79 | 291.48 | 280.6 | 314.38 | 452.04 | 190.99 | 452.71
| Average capacity factor [] | 35.39% | 38.81% | 41.1% | 42.24% | 43.38% | 22.83% | 45.66% | 22.83% | 51.37% |  | [4, 26]
| Average annual full-load hours [MWh_e/MW_e] | 3100 | 3400 | 3600 | 3700 | 3800 | 2000 | 4000 | 2000 | 4500 | [A, L] | 3
Notes:
A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present max. 150m tip height.
A. The full load hours (annual produktion (MWh) per installed power (MW)) depending on the actual location of the wind farm, wake losses and technological characteristics of the individual turbine. The value is an average for the expected locations of the wind farms. FLH also depends on wake losses, noise reduction and technological characteristics of the individual turbine. The level for 2020 is based on expectations from the November 18 auction winners locations and the 2019 prefered technology choice. For 2030 and 2050 a slight increase is assumed based on decrease in specific power and increase in hub height.
B. Modern turbines has typically higher forced outage than older smaller turbines had when they were newer due to more complex technology.
C. Planned outage is typically 1-2 service visits a year, with a maximum duration of one work day, but there can also be planned outage due to shadow flicker stop or sector management (protect turbines at given wind speeds and directions, where they are dense spaced).
D. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
E. The construction time is the periode from FID to commissioning. But from first "dig" to turbines are in operation less than ½ a year is needed for smaller wind farms (clusters), where the similar periode for larger wind farms will be longer. The planning time from idea to construction starts will typically be 2-3 years, but can be essentially more if permitting problems occour.
F. An area of around 50 m x 50 m is needed for a modern wind turbine. Another way of defining the "area use" could be the noise zone, which ranges up to 600-800 m from the wind turbine in worst case.
G. Wind turbines can be downward regulated within very short time and can therefore (if the wind is blowing) be used in both the primary and secondary downward regulation.
H. 2015 Investment costs are based on a number of prospects for projects published in relation to Køberetsordningen. 2020 investment costs are based on updated data from Køberetsordningen. Note that the investment costs listed here includes construction loan interests
I. 75 % of the total yearly O&M costs are assumed to be fixed cost and 25 % are assumed to be variable cost.
K. Currently only turbines up to 150 m total height is installed commercially in Denmark because of strict demands to higher turbines. No change in the national regulation is assumed until after 2020. Some test sites allow for larger turbines. Aboard e.g. in Germany turbines with at total higher of 200 m is installed today.
L. It is expected that the production (FLH) increase 13% from 2015 to 2020 and 3% from 2020-2030 and 1% per decade from 2030-2050
M. Includes development cost.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
2. DTU International Energy Report - Wind Energy, DTU, 2014
3. Master data register of wind turbines at end of December 2014, Danish Energy Agency, 2015
4. Nielsen, P. et. al., Vindmøllers økonomi EUDP projekt 33033-0196, 2010
14. Information from Energinet.dk based on analyses of installed projects (2013-14), published under "Købsretsordningen", 2015
15. Når all-inclusive service alligevel ikke dækker alt, Naturlig Energi, nov. 2014
16. Schwabe, P., Lensink, S. & Hand, M., IEA Wind Task 26: Multi-national case study of the financial cost of wind energy, 2011
18. Hvor længe holder en mølle, Naturlig Energi, januar 2012
25. Analysis of "køberets" projects 2017-18
26. Interviews with project developers and suppliers dec.18-jan.19

## 20 Domestic turbines
Technology |  | Onshore wind turbine, residential - renewable power - wind - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0.03 | 0 | 0.03
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 10% | 2% | 10%
| Planned outage [weeks per year] | 0.16 | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 | B
| Technical lifetime [years] | ctrl: 20; ctrl: 20; ctrl: 20; ctrl: 20
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
| Space requirement [1000 m2/MW_e] | ctrl: 0.8; ctrl: 0.8; ctrl: 0.8; ctrl: 0.8; -: C
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 4.2535 | 4.0408 | 3.8388 | 3.6474 | 3.1901 | 6.3802 | 3.1901 | 6.3802 | [E, F]
| Nominal investment (equipment) [MEUR/MW_e] | 0.95704 | 0.95704 | 0.95704 | 0.95704 | 0.90387 | 1.0102 | 0.90387 | 1.0102 | [E, F]
| Nominal investment (installation) [MEUR/MW_e] | 0.10634 | 0.10634 | 0.10634 | 0.10634 | 0.15951 | 0.053169 | 0.15951 | 0.053169 | [E, F]
| Variable O&M (*total) [EUR/MWh_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [EUR/MW_e/y] | 106337.2718 | 101020.4082 | 95703.5446 | 90386.681 | 0 | 0 | 0 | 0 | G
Technology-specific data
| Fixed O&M (*total) [EUR/unit/y] | 540 | 540 | 540 | 540 | 350 | 700 | 350 | 700 | [E, F]
| Hub height [m] | 18 | 18 | 18 | 18 | 14 | 18 | 14 | 18 | H
| Rotor diameter [m] | 8 | 11 | 12 | 14 | 4 | 14 | 4 | 14 | H
| Average annual full-load hours [MWh_e/MW_e] | 1600 | 1800 | 2000 | 2200 | 1000 | 2300 | 1000 | 2300 | [A, J]
Notes:
A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
B. The maintenance normally consists of 1 -2 annual service visits.
C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
D. Not considered relevant for small domestic turbines.
E. Based on information from manufacturers and resellers. The
F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
G. The service cost is assumed fixed to 100EUR/kW/y.
H. Domestic turbines have a maximum total height of 25 m according to Danish regulations.
J. No development in the capacity factor is expected, because no changing in the size limitation (legislation) is expected. And because location is crucial and one must expect the turbines is put up at the best positions already. But change in legislation i
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
NA. NA

## 21 Offshore turbines
Technology |  | Offshore wind turbines - renewable power - wind - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 8.4 | 15 | 20 | 25 | 30 | 12.75 | 17.25 | 22.5 | 37.5 | A | 1, 2
| Forced outage [] | 1.909% | 1.759% | 1.75% | 1.732% | 1.714% | 1.759% | 1.759% | 1.714% | 1.714% | B
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | B
| Technical lifetime [years] | 27 | 30 | 30 | 30 | 30 | 25 | 35 | 25 | 35 | C
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 3 | 1.5 | 2.5 | D
| Space requirement [1000 m2/MW_e] | 165.36 | 177.36 | 171.96 | 169.84 | 171.26 | 150.76 | 203.96 | 128.44 | 214.07 | E | 3
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) []
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 2.12 | 1.88 | 1.8 | 1.68 | 1.64 | 1.88 | 1.88 | 1.64 | 1.64 | F | 3
| Nominal investment (installation) [MEUR/MW_e] | 0.54 | 0.4 | 0.37 | 0.33 | 0.32 | 0.4 | 0.4 | 0.32 | 0.32 |  | 3
| Nominal investment (project development etc.) [MEUR/MW_e] | 0.38 | 0.31 | 0.28 | 0.25 | 0.23 | 0.26 | 0.36 | 0.17 | 0.34 |  | 3, 6
| Nominal investment (array cables) [MEUR/MW_e] | 0.03 | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.02 | 0.01 | 0.02 |  | 3
| Nominal investment (foundation) [MEUR/MW_e] | 0.21 | 0.21 | 0.22 | 0.22 | 0.21 | 0.18 | 0.25 | 0.16 | 0.32 |  | 3, 4
| Nominal investment (grid connection) [MEUR/MW_e] | 0.25 | 0.24 | 0.24 | 0.25 | 0.26 | 0.2 | 0.28 | 0.2 | 0.4 |  | 3, 5
| Nominal investment (turbines) [MEUR/MW_e] | 0.72 | 0.69 | 0.67 | 0.61 | 0.61 | 0.59 | 0.8 | 0.46 | 0.91 |  | 3
| Variable O&M (*total) [EUR/MWh_e] | 5 | 4.17 | 3.89 | 3.42 | 3.25 | 3.55 | 4.8 | 2.44 | 4.88 | H | 3
| Fixed O&M (*total) [EUR/MW_e/y] | 50000 | 42000 | 39000 | 34000 | 33000 | 35700 | 48300 | 24750 | 49500 | H | 3
Technology-specific data
| Hub height [m] | 103.5 | 138 | 155 | 170 | 185 | 124.2 | 151.8 | 157.25 | 212.75 |  | 1
| Rotor diameter [m] | 167 | 236 | 270 | 300 | 330 | 212.4 | 259.6 | 280.5 | 379.5 |  | 1
| Specific power [W_e/m2] | 383.49 | 342.91 | 349.31 | 353.68 | 350.75 | 359.84 | 325.9 | 364.11 | 331.53 | I | 1
| Specific area coverage [MW_e/km2] | 6.05 | 5.64 | 5.82 | 5.89 | 5.84 | 6.63 | 4.9 | 7.79 | 4.67 | E | 3
| Average annual full-load hours [MWh_e/MW_e] | 4400 | 4775 | 4800 | 4850 | 4900 | 4300 | 5250 | 4050 | 5500 | J | 3
Notes:
A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
E. Calculated based on average spacing of 8 RD between turbines and a square layout. Horns Rev 3 has 9.5, but also quite low wake losses. With 2020 WTG size 8RD corresponds to 6 MW/km^2
F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
G. Other is planning & development, environmental impact assessment, insurances and finance costs.
H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Stiesdal, Offshore wind turbine size prediction tool.xlsx, with changes by Danish Energy Agency.
2. DTU Wind Energy: Pushing the physics of the large turbines of the future. 2021. Published in DTU International Energy Report 2021: Perspectives on Wind Energy. https://doi.org/10.11581/DTU.00000208
3. EMD cost and AEP Excel calculation tool
4. EA Energy Analyse/Cowi April 20 slide 25: https://www.ea-energianalyse.dk/wp-content/uploads/2020/05/1949_Offshore-wind-and-infrastructure.pdf
5. From ENS 2021: FT - omkostninger Anholt, HR3, KF.xlsx
6. Interview with Per Stenholt, Vattenfall, November 21

## 21 Near shore turbines
Technology |  | Offshore wind turbines, nearshore - renewable power - wind - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 8.4 | 10 | 15 | 15 | 15 | 8.5 | 11.5 | 11.25 | 18.75 | A | 1, 2
| Forced outage [] | 2.048% | 1.942% | 1.887% | 1.887% | 1.887% | 1.942% | 1.942% | 1.887% | 1.887% | B
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | B
| Technical lifetime [years] | 27 | 30 | 30 | 30 | 30 | 25 | 35 | 25 | 35 | C
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 3 | 1.5 | 2.5 | D
| Space requirement [1000 m2/MW_e] | 32.02 | 35.18 | 35.81 | 35.81 | 35.81 | 29.91 | 40.46 | 26.86 | 44.76 | E | 3
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) []
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.7 | 1.49 | 1.38 | 1.24 | 1.19 | 1.49 | 1.49 | 1.19 | 1.19 | F | 3
| Nominal investment (installation) [MEUR/MW_e] | 0.39 | 0.31 | 0.25 | 0.23 | 0.22 | 0.31 | 0.31 | 0.22 | 0.22 |  | 3
| Nominal investment (project development etc.) [MEUR/MW_e] | 0.39 | 0.33 | 0.29 | 0.26 | 0.25 | 0.28 | 1.31 | 0.18 | 0.98 |  | 3, 6
| Nominal investment (array cables) [MEUR/MW_e] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 0.01 | 0.04 |  | 3
| Nominal investment (foundation) [MEUR/MW_e] | 0.13 | 0.13 | 0.12 | 0.11 | 0.11 | 0.11 | 0.51 | 0.08 | 0.42 |  | 3, 4
| Nominal investment (grid connection) [MEUR/MW_e] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.2 | 0.04 | 0.19 |  | 3, 5
| Nominal investment (turbines) [MEUR/MW_e] | 0.72 | 0.66 | 0.65 | 0.58 | 0.56 | 0.56 | 2.63 | 0.42 | 2.24 |  | 3
| Variable O&M (*total) [EUR/MWh_e] | 5 | 4.17 | 3.89 | 3.42 | 3.25 | 3.55 | 16.69 | 2.44 | 13.01 | H | 3
| Fixed O&M (*total) [EUR/MW_e/y] | 50000 | 42000 | 39000 | 34000 | 33000 | 35700 | 48300 | 24750 | 49500 | H | 3
Technology-specific data
| Hub height [m] | 103.5 | 115.5 | 138 | 138 | 138 | 98.17 | 132.82 | 103.5 | 207 |  | 1
| Rotor diameter [m] | 167 | 191 | 236 | 236 | 236 | 162.35 | 219.65 | 177 | 354 |  | 1
| Specific power [W_e/m2] | 383.49 | 349.01 | 342.91 | 342.91 | 342.91 | 410.61 | 303.49 | 457.21 | 190.5 | I | 1
| Specific area coverage [MW_e/km2] | 31.23 | 28.42 | 27.92 | 27.92 | 27.92 | 33.44 | 24.71 | 37.23 | 22.34 | E | 3
| Average annual full-load hours [MWh_e/MW_e] | 4100 | 4325 | 4450 | 4450 | 4450 | 3675 | 4975 | 3250 | 6500 | J | 3
Notes:
A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
E. For Nearshore the space requirements becomes "artificial", while typically 1-row projects will be expected. The space is here calculated based on square layout to give a number.
F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
G. Other is planning & development, environmental impact assessment, insurances and finance costs.
H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Stiesdal, Offshore wind turbine size prediction tool.xlsx, with changes by Danish Energy Agency.
2. DTU Wind Energy: Pushing the physics of the large turbines of the future. 2021. Published in DTU International Energy Report 2021: Perspectives on Wind Energy. https://doi.org/10.11581/DTU.00000208
3. EMD cost and AEP Excel calculation tool
4. EA Energy Analyse/Cowi April 20 slide 25: https://www.ea-energianalyse.dk/wp-content/uploads/2020/05/1949_Offshore-wind-and-infrastructure.pdf
5. From ENS 2021: FT - omkostninger Anholt, HR3, KF.xlsx
6. Interview with Per Stenholt, Vattenfall, November 21

## 22 Rooftop PV residential
Technology |  | PV - renewable power - solar - residential rooftop
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; -: B3,C
Forced outage [] | bar: ctrl to ctrl
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Space requirement [1000 m2/MW_e] | ctrl: 6.36; ctrl: 5.12; ctrl: 4.57; ctrl: 4.29; ctrl: 4.04; -: 6
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.67 | 1.24 | 0.84 | 0.7 | 0.64 | 1.19 | 1.3 | 0.54 | 0.85 | M,O | 2, 4
| Nominal investment (*total, per DC) [MEUR/MW_e] | 1.59 | 1.18 | 0.8 | 0.67 | 0.61 | 1.13 | 1.24 | 0.52 | 0.81 | M,N | 2, 4
| Nominal investment (grid connection) [MEUR/MW_e] |  | 0.03 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02
| Nominal investment (inverter) [MEUR/MW_e] |  | 0.22 | 0.14 | 0.12 | 0.1 | 0.21 | 0.23 | 0.09 | 0.12
| Nominal investment (pv modules) [MEUR/MW_e] | 0.81 | 0.49 | 0.27 | 0.2 | 0.17 | 0.47 | 0.51 | 0.14 | 0.33 | M,O
| Nominal investment (installation) [MEUR/MW_e] |  | 0.13 | 0.11 | 0.09 | 0.09 | 0.13 | 0.14 | 0.08 | 0.1
| Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | 0.86 | 0.21 | 0.17 | 0.15 | 0.14 | 0.2 | 0.22 | 0.13 | 0.16
Nominal investment (soft costs) [MEUR/MW_e]
| Fixed O&M (*total) [EUR/MW_e/y] | 16700 | 13400 | 10700 | 9600 | 8900 | 12100 | 14800 | 8100 | 9900 | P
Fixed O&M (land rent) [EUR/MW_e/y]
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; -: B3,C
| Space requirement (per DC) [1000m2/MW_e] | ctrl: 6.06; ctrl: 4.88; ctrl: 4.35; ctrl: 4.08; ctrl: 3.85; -: 6
| Nominal investment (installation, per DC) [MEUR/MW_e] |  | 0.27 | 0.22 | 0.19 | 0.18 | 0.26 | 0.28 | 0.16 | 0.2
| Nominal investment (inverter, per DC) [MEUR/MW_e] |  | 0.21 | 0.14 | 0.11 | 0.1 | 0.2 | 0.22 | 0.08 | 0.12
| Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | 0.82 | 0.2 | 0.16 | 0.15 | 0.14 | 0.19 | 0.21 | 0.12 | 0.15
| Nominal investment (pv module, per DC) [MEUR/MW_e] | 0.78 | 0.47 | 0.26 | 0.19 | 0.17 | 0.45 | 0.49 | 0.13 | 0.31 | M,O
| Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] |  | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02
| Fixed O&M (*total, per DC) [EUR/MW_e/y] | 15900 | 12800 | 10200 | 9100 | 8500 | 11500 | 14100 | 7700 | 9400 | P
Fixed O&M (land rent, per DC) [EUR/MW_e/y]
| Fixed O&M (other, per DC) [EUR/MW_e/y] | ctrl: 12800; ctrl: 10200; ctrl: 9100; ctrl: 8500
| Average annual degradation of full-load hours [] | ctrl: 0.5%; ctrl: 0.4%; ctrl: 0.3%; ctrl: 0.3%; ctrl: 0.3%
| Global horizontal irradiance [kWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Transposition factor | ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; -: E
| Performance ratio (contribution from bifaciality) [] | -: 3
| Performance ratio (measure of combined losses) [] | ctrl: 79%; ctrl: 85%; ctrl: 90%; ctrl: 91%; ctrl: 92%; -: F
| PV module conversion efficiency [] | 16.5% | 20.5% | 23% | 24.5% | 26% |  |  |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; -: 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 |  |  |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 934.72; ctrl: 1010.33; ctrl: 1116.06; ctrl: 1127.81; ctrl: 1139.56; -: A1,I
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 981.46; ctrl: 1060.84; ctrl: 1171.86; ctrl: 1184.2; ctrl: 1196.53; -: A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Rooftop PV comm.&industrial
Technology |  | PV - renewable power - solar - commercial/industrial rooftop
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; -: B2,C
Forced outage [] | bar: ctrl to ctrl
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Space requirement [1000 m2/MW_e] | ctrl: 6.67; ctrl: 5.37; ctrl: 4.78; ctrl: 4.49; ctrl: 4.23; -: 6
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.43 | 0.87 | 0.57 | 0.46 | 0.41 | 0.86 | 0.92 | 0.36 | 0.59 | M,O | 2, 4
| Nominal investment (*total, per DC) [MEUR/MW_e] | 1.3 | 0.79 | 0.51 | 0.42 | 0.38 | 0.78 | 0.84 | 0.33 | 0.53 | M,N | 2, 4
| Nominal investment (grid connection) [MEUR/MW_e] |  | 0.04 | 0.04 | 0.03 | 0.03 | 0.04 | 0.05 | 0.03 | 0.03
| Nominal investment (inverter) [MEUR/MW_e] |  | 0.17 | 0.11 | 0.09 | 0.08 | 0.17 | 0.18 | 0.07 | 0.1
| Nominal investment (pv modules) [MEUR/MW_e] | 0.81 | 0.44 | 0.24 | 0.18 | 0.15 | 0.43 | 0.46 | 0.12 | 0.29 | M,O
| Nominal investment (installation) [MEUR/MW_e] |  | 0.13 | 0.11 | 0.09 | 0.09 | 0.13 | 0.14 | 0.08 | 0.1
| Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | 0.61 | 0.09 | 0.07 | 0.06 | 0.06 | 0.09 | 0.09 | 0.05 | 0.07
Nominal investment (soft costs) [MEUR/MW_e]
| Fixed O&M (*total) [EUR/MW_e/y] | 14300 | 10600 | 8900 | 8000 | 7500 | 9500 | 11700 | 6700 | 8300 | P
Fixed O&M (land rent) [EUR/MW_e/y]
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; -: B2,C
| Space requirement (per DC) [1000m2/MW_e] | 6.06 | 4.88 | 4.35 | 4.08 | 3.85 |  |  |  |  | W | 6
| Nominal investment (installation, per DC) [MEUR/MW_e] |  | 0.12 | 0.1 | 0.09 | 0.08 | 0.12 | 0.13 | 0.07 | 0.09
| Nominal investment (inverter, per DC) [MEUR/MW_e] |  | 0.16 | 0.1 | 0.08 | 0.07 | 0.16 | 0.17 | 0.06 | 0.09
| Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | 0.56 | 0.08 | 0.06 | 0.06 | 0.05 | 0.08 | 0.08 | 0.05 | 0.06
| Nominal investment (pv module, per DC) [MEUR/MW_e] | 0.74 | 0.4 | 0.22 | 0.16 | 0.14 | 0.39 | 0.42 | 0.11 | 0.26 | M,O
| Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] |  | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03
| Fixed O&M (*total, per DC) [EUR/MW_e/y] | 13000 | 9600 | 8100 | 7300 | 6800 | 8600 | 10600 | 6100 | 7500 | P
Fixed O&M (land rent, per DC) [EUR/MW_e/y]
| Fixed O&M (other, per DC) [EUR/MW_e/y] | ctrl: 13000; ctrl: 9600; ctrl: 8100; ctrl: 7300; ctrl: 6800
| Average annual degradation of full-load hours [] | ctrl: 0.5%; ctrl: 0.4%; ctrl: 0.3%; ctrl: 0.3%; ctrl: 0.3%
| Global horizontal irradiance [kWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Transposition factor | ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; -: E
| Performance ratio (contribution from bifaciality) [] | ctrl: 0%; ctrl: 0%; ctrl: 0%; ctrl: 1%; ctrl: 2%; -: 3
| Performance ratio (measure of combined losses) [] | ctrl: 81%; ctrl: 85%; ctrl: 90%; ctrl: 91%; ctrl: 92%; -: F
| PV module conversion efficiency [] | 16.5% | 20.5% | 23% | 24.5% | 26% |  |  |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; -: 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 |  |  |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 950.59; ctrl: 1010.33; ctrl: 1116.06; ctrl: 1127.81; ctrl: 1139.56; -: A1,I
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1045.65; ctrl: 1111.36; ctrl: 1227.67; ctrl: 1240.59; ctrl: 1253.51; -: A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Utility-scale PV
Technology |  | PV - renewable power - solar - utility-scale, ground mounted
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 4; ctrl: 40; ctrl: 40; ctrl: 40; ctrl: 40
Forced outage [] | bar: ctrl to ctrl
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5
| Space requirement [1000 m2/MW_e] | 20.25 | 13.75 | 12.26 | 11.51 | 10.84 |  |  |  |  | B,B1 | 6
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 1.55 | 0.56 | 0.38 | 0.32 | 0.29 | 0.54 | 0.6 | 0.25 | 0.4 | M,N,O,Q | 2, 4
| Nominal investment (*total, per DC) [MEUR/MW_e] | 1.15 | 0.45 | 0.31 | 0.26 | 0.23 | 0.44 | 0.48 | 0.2 | 0.32 | M,N,O,Q | 2, 4
| Nominal investment (grid connection) [MEUR/MW_e] | 0.09 | 0.06 | 0.05 | 0.04 | 0.04 | 0.06 | 0.07 | 0.04 | 0.05
| Nominal investment (inverter) [MEUR/MW_e] | 0.11 | 0.03 | 0.02 | 0.02 | 0.01 | 0.03 | 0.03 | 0.01 | 0.02
| Nominal investment (pv modules) [MEUR/MW_e] | 0.89 | 0.26 | 0.14 | 0.11 | 0.09 | 0.25 | 0.27 | 0.07 | 0.17
| Nominal investment (installation) [MEUR/MW_e] | 0.14 | 0.13 | 0.1 | 0.09 | 0.09 | 0.12 | 0.14 | 0.08 | 0.1
| Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | 0.23 | 0.05 | 0.04 | 0.04 | 0.03 | 0.05 | 0.05 | 0.03 | 0.04
| Nominal investment (soft costs) [MEUR/MW_e] | 0.09 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03 | V
| Fixed O&M (*total) [EUR/MW_e/y] | 13600 | 11300 | 9500 | 8100 | 7400 | 10100 | 12400 | 6600 | 8100
| Fixed O&M (land rent) [EUR/MW_e/y] | ctrl: 4400; ctrl: 3900; ctrl: 3100; ctrl: 2500; -: S
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 5.4; ctrl: 50; ctrl: 50; ctrl: 50; ctrl: 50; -: C
| Space requirement (per DC) [1000m2/MW_e] | 15 | 11 | 9.8 | 9.2 | 8.67 |  |  |  |  | B,B1 | 6
| Nominal investment (installation, per DC) [MEUR/MW_e] | 0.11 | 0.1 | 0.08 | 0.07 | 0.07 | 0.1 | 0.11 | 0.06 | 0.08 | V
| Nominal investment (inverter, per DC) [MEUR/MW_e] | 0.08 | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.03 | 0.01 | 0.01
| Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] | 0.17 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03
| Nominal investment (pv module, per DC) [MEUR/MW_e] | 0.66 | 0.21 | 0.11 | 0.08 | 0.07 | 0.2 | 0.22 | 0.06 | 0.14
| Nominal investment (soft costs, per DC) [MEUR/MW_e] | 0.06 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | V
| Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] | 0.06 | 0.05 | 0.04 | 0.04 | 0.03 | 0.05 | 0.05 | 0.03 | 0.04 | R
| Fixed O&M (*total, per DC) [EUR/MW_e/y] | 10100 | 9000 | 7600 | 6500 | 5900 | 8100 | 9900 | 5300 | 6500
| Fixed O&M (land rent, per DC) [EUR/MW_e/y] | ctrl: 3500; ctrl: 3100; ctrl: 2500; ctrl: 2000; -: S; -: 6
| Fixed O&M (other, per DC) [EUR/MW_e/y] | ctrl: 5500; ctrl: 4500; ctrl: 4000; ctrl: 3900; -: P2
| Average annual degradation of full-load hours [] | 0.5% | 0.4% | 0.3% | 0.3% | 0.3% | 0.3% | 0.5% |  |  | A2
| Global horizontal irradiance [kWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Transposition factor | ctrl: 1.15; ctrl: 1.17; ctrl: 1.17; ctrl: 1.17; ctrl: 1.17; -: E
| Performance ratio (contribution from bifaciality) [] | 0% | 1% | 5% | 5% | 5% |  |  |  |  | H | 3
| Performance ratio (measure of combined losses) [] | ctrl: 81%; ctrl: 86%; ctrl: 95%; ctrl: 96%; ctrl: 97%; -: F
| PV module conversion efficiency [] | 16.5% | 20.5% | 23% | 24.5% | 26% | 20% | 21% |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; -: 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.35 | 1.25 | 1.25 | 1.25 | 1.25 |  |  |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 981.33; ctrl: 1074.62; ctrl: 1187.08; ctrl: 1199.58; ctrl: 1212.07; -: A1, K
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1324.8; ctrl: 1343.28; ctrl: 1483.85; ctrl: 1499.47; ctrl: 1515.09; -: A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Utility-scale PV tracker
Technology |  | PV - renewable power - solar - utility-scale ground mounted, single axis tracking
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 40; ctrl: 40; ctrl: 40; ctrl: 40
Forced outage [] | bar: ctrl to ctrl
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5
| Space requirement [1000 m2/MW_e] | ctrl: 17.88; ctrl: 15.93; ctrl: 14.96; ctrl: 14.09; -: B,B1; -: 6
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0 | 0.65 | 0.45 | 0.38 | 0.35 | 0.6 | 0.7 | 0.29 | 0.47 | M,N,O,Q | 2, 4
| Nominal investment (*total, per DC) [MEUR/MW_e] | 0 | 0.52 | 0.36 | 0.31 | 0.28 | 0.48 | 0.56 | 0.23 | 0.38 | M,N,O,Q | 2, 4
| Nominal investment (grid connection) [MEUR/MW_e] | 0 | 0.06 | 0.05 | 0.04 | 0.04 | 0.06 | 0.07 | 0.04 | 0.05
| Nominal investment (inverter) [MEUR/MW_e] | 0 | 0.03 | 0.02 | 0.02 | 0.01 | 0.03 | 0.03 | 0.01 | 0.02
| Nominal investment (pv modules) [MEUR/MW_e] | 0 | 0.26 | 0.14 | 0.11 | 0.09 | 0.24 | 0.28 | 0.07 | 0.17
| Nominal investment (tracker related costs) [MEUR/MW_e] | 0 | 0.09 | 0.07 | 0.06 | 0.06 | 0.08 | 0.09 | 0.05 | 0.07 | T
| Nominal investment (installation) [MEUR/MW_e] | 0 | 0.13 | 0.1 | 0.09 | 0.09 | 0.12 | 0.14 | 0.07 | 0.1
| Nominal investment (other, i.e. residual balance of plant) [MEUR/MW_e] | 0 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.02 | 0.03
| Nominal investment (soft costs) [MEUR/MW_e] | 0 | 0.05 | 0.04 | 0.04 | 0.03 | 0.04 | 0.05 | 0.03 | 0.04 | V
| Fixed O&M (*total) [EUR/MW_e/y] | 0 | 12100 | 10400 | 9400 | 9000 | 10900 | 13400 | 8100 | 9900 | P2
| Fixed O&M (land rent) [EUR/MW_e/y] | ctrl: 0; ctrl: 5300; ctrl: 4800; ctrl: 4400; ctrl: 4100; -: S
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 50; ctrl: 50; ctrl: 50; ctrl: 50; -: C
| Space requirement (per DC) [1000m2/MW_e] | ctrl: 14.3; ctrl: 12.75; ctrl: 11.97; ctrl: 11.28; -: B,B1; -: 6
| Nominal investment (installation, per DC) [MEUR/MW_e] |  | 0.1 | 0.08 | 0.07 | 0.07 | 0.09 | 0.11 | 0.06 | 0.08 | V
| Nominal investment (inverter, per DC) [MEUR/MW_e] |  | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.03 | 0.01 | 0.01
| Nominal investment (other, i.e. residual balance of plant, per DC) [MEUR/MW_e] |  | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02
| Nominal investment (pv module, per DC) [MEUR/MW_e] |  | 0.21 | 0.11 | 0.08 | 0.07 | 0.19 | 0.22 | 0.05 | 0.14
| Nominal investment (soft costs, per DC) [MEUR/MW_e] |  | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03 | V
| Nominal investment (tracker related cost, per DC) [MEUR/MW_e] |  | 0.07 | 0.06 | 0.05 | 0.05 | 0.06 | 0.08 | 0.04 | 0.05 | T
| Nominal investment (transformer and grid connection, per DC) [MEUR/MW_e] |  | 0.05 | 0.04 | 0.04 | 0.03 | 0.04 | 0.05 | 0.03 | 0.04 | R
| Fixed O&M (*total, per DC) [EUR/MW_e/y] |  | 9700 | 8300 | 7500 | 7200 | 8700 | 10700 | 6500 | 7900
| Fixed O&M (land rent, per DC) [EUR/MW_e/y] | ctrl: 4200; ctrl: 3800; ctrl: 3500; ctrl: 3300; -: S; -: 6
| Fixed O&M (other, per DC) [EUR/MW_e/y] | ctrl: 5500; ctrl: 4500; ctrl: 4000; ctrl: 3900; -: P2
| Average annual degradation of full-load hours [] |  | 0.4% | 0.3% | 0.3% | 0.3% | 0.3% | 0.5% |  |  | A2
| Global horizontal irradiance [kWh/m2/y] | ctrl: 1068; ctrl: 1068; ctrl: 1068; ctrl: 1068; -: A; -: 1
| Transposition factor | ctrl: 1.35; ctrl: 1.35; ctrl: 1.35; ctrl: 1.35; -: E
| Performance ratio (contribution from bifaciality) [] | ctrl: 1%; ctrl: 5%; ctrl: 5%; ctrl: 5%; -: H; -: 3
| Performance ratio (measure of combined losses) [] | ctrl: 86%; ctrl: 95%; ctrl: 96%; ctrl: 97%; -: F
| PV module conversion efficiency [] |  | 20.5% | 23% | 24.5% | 26% | 20% | 21% |  |  | U | 3
| Inverter lifetime [years] | ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; -: 6
| Sizing factor (DC/AC) [W_e/W_e] | ctrl: 1.25; ctrl: 1.25; ctrl: 1.25; ctrl: 1.25; -: D; -: 5, 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 1235.81; ctrl: 1369.71; ctrl: 1379.51; ctrl: 1393.88; -: A1, K
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1544.77; ctrl: 1712.14; ctrl: 1724.39; ctrl: 1742.36; -: A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 23 Wave Energy
Technology |  | Wave power - renewable power - wave - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | -: [1, 1, 4, 4]
| Generating capacity for one unit [MW_e] | lower: 2; upper: 50; lower: 50; upper: 500
| Technical lifetime [years] | ctrl: 10; ctrl: 20; ctrl: 25; ctrl: 30; -: 4
| Construction time [years] | ctrl: 3.5; ctrl: 3.5; ctrl: 3.5; -: C; -: 4
| Construction time [years] | lower: 3; upper: 4; lower: 3; upper: 4
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0 | 0 | 0 | 1.7014 | 0 | 0 | 0 | 0 | [A, B] | [2, 2, 2, 3]
| Nominal investment (*total) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 4.0408 | 9.5704 | 0 | 0 | 0
| Variable O&M (*total) [2011-EUR/MWh_e] | 21.2675 | 15.9506 | 10.6337 | 7.4436 | 0 | 0 | 0 | 0 | 0 | 4
Technology-specific data
| Availability [] | ctrl: 90%; ctrl: 95%; ctrl: 97%; ctrl: 98%; -: 4
| Length of installation of one power plant [km] | -: [1, 1, 4, 4]
| Length of installation of one power plant [km] | lower: 0.2; upper: 5; lower: 5; upper: 100
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1500; ctrl: 2500; ctrl: 3500; ctrl: 4500; -: 4
Notes:
A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning curve effect have been achieved.
B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
C. Much dependent on plant size and location.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Wave Net final report, Project no. ERK5 - CT -1999-20001 (2000 - 2003)
2. "Energy Technology Perspectives 2008", International Energy Agency, 2008.
3. "Energy Technology Perspectives 2010", International Energy Agency, 2010.
4. Danish Wave Energy Association, 2012

## 40 Comp. hp, airsource 1 MW
Technology |  | Heat pump, air source - heat pump - electricity - small
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 1 | 1 | 1 | 1 | 1 | 0.3 | 1.5 | 0.2 | 1.5
| Heat efficiency (net, annual average) [] | 290% | 295% | 300% | 310% | 315% | 275% | 335% | 285% | 355% | [A, A1, B, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 255% | 260% | 265% | 275% | 280% | 240% | 300% | 250% | 320% | [A, A1, B, C] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | E | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [F, G] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 1 | 1 | 1 | 1 | 1 | 0.7 | 2 | 0.7 | 2 | Q | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | H | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | H | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [H, J] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [H, I] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 1.5206 | 1.5206 | 1.4143 | 1.4143 | 1.4143 | 1.0102 | 2.0204 | 1.0102 | 2.0204 | [A, K, L, P, Q] | [1, 14, 15]
| Nominal investment (equipment) [MEUR/MW_h] | 1.1378 | 1.1378 | 1.0634 | 1.0634 | 1.0634 | 0.75499 | 1.5206 | 0.75499 | 1.5206 | A | [1, 14, 15]
| Nominal investment (grid connection) [MEUR/MW_e] | 0.031901 | 0.031901 | 0.031901 | 0.031901 | 0.031901 | 0.021267 | 0.20204 | 0.021267 | 0.20204 | K | [1, 14, 15]
| Nominal investment (installation) [MEUR/MW_h] | 0.27648 | 0.27648 | 0.25521 | 0.25521 | 0.25521 | 0.18077 | 0.20204 | 0.18077 | 0.20204 | A | [1, 14, 15]
| Variable O&M (*total) [EUR/MWh_h] | 2.8605 | 2.8605 | 2.8605 | 2.8605 | 2.8605 | 2.3075 | 3.3709 | 2.3075 | 3.3709 |  | [1, 14, 15]
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [E, N] | [1, 14, 15]
| Variable O&M (other O&M) [EUR/MWh_h] | 2.8605 | 2.8605 | 2.8605 | 2.8605 | 2.8605 | 2.3075 | 3.3709 | 2.3075 | 3.3709 | M | [1, 14, 15]
| Fixed O&M (*total) [EUR/MW_h/y] | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 1063.3727 | 3190.1182 | 1063.3727 | 5316.8636 | M | [1, 14, 15]
| Startup cost [EUR/MW_h/startup] | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 5.3169 | 21.2675 | 2.1267 | 21.2675 | O | 15
Technology-specific data
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Includes energy consumption for defrosting and auxiliary electricity consumption.
C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F. Does not include tendering and regulatory approvals.
G. The development within construction time will depend on future production figures and standardization of plants.
H. The regulation ablility will depend on the future markets for regulation services.
I. Cold start of time is starting a heat pump where stand by heating has not been applied
J. Operation at part load will usually increase COP but also variable O&M costs
K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L. Land is usually owned by the company
M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O. 1/4 MWh-heat per MW is lost during startup
P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 15 % as compontents must be rated for higher pressure levels
Q. Including land for air coolers
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, airsource 3 MW
Technology |  | Heat pump, air source - heat pump - electricity - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 3 | 3 | 3 | 3 | 3 | 1.5 | 5 | 1.5 | 5
| Heat efficiency (net, annual average) [] | 340% | 350% | 360% | 365% | 370% | 320% | 370% | 330% | 380% | [A, A1, B, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 310% | 315% | 320% | 330% | 340% | 290% | 330% | 300% | 350% | [A, A1, B, C] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | E | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 1 | 0.4 | 1 | [F, G] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 1.2 | 0.5 | 1.2 | Q | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 100% | 5% | 100% | H | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | H | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [H, J] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [H, I] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 1.0102 | 1.0102 | 0.9145 | 0.9145 | 0.9145 | 0.80816 | 1.5206 | 0.71246 | 1.5206 | [A, K, L, P, Q] | [1, 14, 15]
| Nominal investment (equipment) [MEUR/MW_h] | 0.80816 | 0.80816 | 0.72309 | 0.72309 | 0.72309 | 0.64866 | 1.2122 | 0.56359 | 1.2122 | A | [1, 14, 15]
| Nominal investment (grid connection) [MEUR/MW_e] | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.14887 | 0.010634 | 0.14887 | K | [1, 14, 15]
| Nominal investment (installation) [MEUR/MW_h] | 0.18077 | 0.18077 | 0.15951 | 0.15951 | 0.15951 | 0.14887 | 0.14887 | 0.1276 | 0.14887 | A | [1, 14, 15]
| Variable O&M (*total) [EUR/MWh_h] | 2.3288 | 2.3288 | 2.6691 | 2.3288 | 2.8392 | 2.3288 | 3.9238 | 2.3288 | 2.3288 |  | [1, 14, 15]
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [E, N] | [1, 14, 15]
| Variable O&M (other O&M) [EUR/MWh_h] | 2.3288 | 2.3288 | 2.6691 | 2.3288 | 2.8392 | 2.3288 | 3.9238 | 2.3288 | 2.3288 | M | [1, 14, 15]
| Fixed O&M (*total) [EUR/MW_h/y] | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 1063.3727 | 3190.1182 | 1063.3727 | 5316.8636 | M | [1, 14, 15]
| Startup cost [EUR/MW_h/startup] | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 5.3169 | 21.2675 | 2.1267 | 21.2675 | O | 15
Technology-specific data
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Includes energy consumption for defrosting and auxiliary electricity consumption.
C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F. Does not include tendering and regulatory approvals.
G. The development within construction time will depend on future production figures and standardization of plants.
H. The regulation ablility will depend on the future markets for regulation services.
I. Cold start of time is starting a heat pump where stand by heating has not been applied
J. Operation at part load will usually increase COP but also variable O&M costs
K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L. Land is usually owned by the company
M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O. 1/4 MWh-heat per MW is lost during startup
P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
Q. Including land for air coolers
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, airsource 10 MW
Technology |  | Heat pump, air source - heat pump - electricity - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | 20
| Heat efficiency (net, annual average) [] | 380% | 380% | 385% | 390% | 390% | 360% | 400% | 360% | 410% | [A, A1, B, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 350% | 350% | 355% | 360% | 360% | 330% | 370% | 330% | 380% | [A, A1, B, C] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | E | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 1 | 0.4 | 1 | [F, G] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 1 | 0.4 | 1 | Q | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 100% | 5% | 100% | H | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | H | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [H, J] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [H, I] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.9145 | 0.9145 | 0.80816 | 0.80816 | 0.80816 | 0.71246 | 1.2122 | 0.71246 | 1.2122 | [A, K, L, P, Q] | [1, 14, 15]
| Nominal investment (equipment) [MEUR/MW_h] | 0.72309 | 0.72309 | 0.64866 | 0.64866 | 0.64866 | 0.56359 | 0.96767 | 0.56359 | 0.96767 | A | [1, 14, 15]
| Nominal investment (grid connection) [MEUR/MW_e] | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.010634 | 0.11697 | 0.010634 | 0.11697 | K | [1, 14, 15]
| Nominal investment (installation) [MEUR/MW_h] | 0.15951 | 0.15951 | 0.14887 | 0.14887 | 0.14887 | 0.1276 | 0.11697 | 0.1276 | 0.11697 | A | [1, 14, 15]
| Variable O&M (*total) [EUR/MWh_h] | 1.7971 | 1.7971 | 1.7971 | 1.7971 | 1.7971 | 1.0634 | 2.8605 | 1.0634 | 2.8605 |  | [1, 14, 15]
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [E, N] | [1, 14, 15]
| Variable O&M (other O&M) [EUR/MWh_h] | 1.7971 | 1.7971 | 1.7971 | 1.7971 | 1.7971 | 1.5951 | 2.8605 | 1.5951 | 2.8605 | M | [1, 14, 15]
| Fixed O&M (*total) [EUR/MW_h/y] | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 1063.3727 | 3190.1182 | 1063.3727 | 5316.8636 | M | [1, 14, 15]
| Startup cost [EUR/MW_h/startup] | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 5.3169 | 21.2675 | 2.1267 | 21.2675 | O | 15
Technology-specific data
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Includes energy consumption for defrosting and auxiliary electricity consumption.
C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F. Does not include tendering and regulatory approvals.
G. The development within construction time will depend on future production figures and standardization of plants.
H. The regulation ablility will depend on the future markets for regulation services.
I. Cold start of time is starting a heat pump where stand by heating has not been applied
J. Operation at part load will usually increase COP but also variable O&M costs
K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L. Land is usually owned by the company
M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O. 1/4 MWh-heat per MW is lost during startup
P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
Q. Including land for air coolers
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 1 MW
Technology |  | Heat pump, industrial excess heat - heat pump - electricity - small
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 1 | 1 | 1 | 1 | 1 | 0.3 | 1.5 | 0.2 | 1.5
| Heat efficiency (net, annual average) [] | 410% | 420% | 430% | 440% | 450% | 410% | 450% | 410% | 480% | [A, A1, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 400% | 410% | 420% | 430% | 440% | 400% | 430% | 400% | 450% | [A, A1, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.2 |  | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 1.3186 | 1.3186 | 1.2122 | 1.2122 | 1.2122 | 1.0102 | 2.0204 | 1.0102 | 2.0204 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [MEUR/MW_h] | 0.98894 | 0.98894 | 0.9145 | 0.9145 | 0.9145 | 0.75499 | 1.5206 | 0.75499 | 1.5206 | A | [1, 14, 15]
| Nominal investment (grid connection) [MEUR/MW_e] | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.20204 | 0.021267 | 0.20204 | J | [1, 14, 15]
| Nominal investment (installation) [MEUR/MW_h] | 0.23394 | 0.23394 | 0.22331 | 0.22331 | 0.22331 | 0.18077 | 0.20204 | 0.18077 | 0.20204 | A | [1, 14, 15]
| Variable O&M (*total) [EUR/MWh_h] | 2.8605 | 2.8605 | 2.8605 | 3.2858 | 3.3709 | 1.7971 | 2.8605 | 2.8605 | 3.3709 |  | [1, 14, 15]
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [D, M] | [1, 14, 15]
| Variable O&M (other O&M) [EUR/MWh_h] | 2.8605 | 2.8605 | 2.8605 | 3.2858 | 3.3709 | 1.7971 | 2.8605 | 2.8605 | 3.3709 | L | [1, 14, 15]
| Fixed O&M (*total) [EUR/MW_h/y] | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 1063.3727 | 3190.1182 | 1063.3727 | 5316.8636 | L | [1, 14, 15]
| Startup cost [EUR/MW_h/startup] | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 5.3169 | 21.2675 | 2.1267 | 21.2675 | N | 15
Technology-specific data
Notes:
A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 15 % as compontents must be rated for higher pressure levels
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 3 MW
Technology |  | Heat pump, industrial excess heat - heat pump - electricity - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 3 | 3 | 3 | 3 | 3 | 1.5 | 5 | 1.5 | 5
| Heat efficiency (net, annual average) [] | 460% | 470% | 480% | 490% | 500% | 450% | 490% | 460% | 520% | [A, A1, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 450% | 460% | 470% | 480% | 490% | 440% | 480% | 450% | 510% | [A, A1, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.1 | 0.03 | 0.1 |  | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.9145 | 0.9145 | 0.80816 | 0.80816 | 0.80816 | 0.71246 | 1.2122 | 0.71246 | 1.2122 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [MEUR/MW_h] | 0.72309 | 0.72309 | 0.64866 | 0.64866 | 0.64866 | 0.56359 | 0.96767 | 0.56359 | 0.96767 | A | [1, 14, 15]
| Nominal investment (grid connection) [MEUR/MW_e] | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.010634 | 0.11697 | 0.010634 | 0.11697 | J | [1, 14, 15]
| Nominal investment (installation) [MEUR/MW_h] | 0.15951 | 0.15951 | 0.14887 | 0.14887 | 0.14887 | 0.1276 | 0.11697 | 0.1276 | 0.11697 | A | [1, 14, 15]
| Variable O&M (*total) [EUR/MWh_h] | 2.3288 | 2.3288 | 2.6691 | 2.3288 | 2.8392 | 2.3288 | 2.3288 | 2.3075 | 2.3288 |  | [1, 14, 15]
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [D, M] | [1, 14, 15]
| Variable O&M (other O&M) [EUR/MWh_h] | 2.3288 | 2.3288 | 2.6691 | 2.3288 | 2.8392 | 2.3288 | 2.3288 | 2.3075 | 2.3288 | L | [1, 14, 15]
| Fixed O&M (*total) [EUR/MW_h/y] | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 1063.3727 | 3190.1182 | 1063.3727 | 5316.8636 | L | [1, 14, 15]
| Startup cost [EUR/MW_h/startup] | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 5.3169 | 21.2675 | 2.1267 | 21.2675 | N | 15
Technology-specific data
Notes:
A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 10 MW
Technology |  | Heat pump, industrial excess heat - heat pump - electricity - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | 20
| Heat efficiency (net, annual average) [] | 510% | 520% | 530% | 540% | 550% | 500% | 530% | 510% | 570% | [A, A1, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 500% | 510% | 520% | 530% | 540% | 490% | 520% | 500% | 560% | [A, A1, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 |  | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.71246 | 0.71246 | 0.60612 | 0.60612 | 0.60612 | 0.51042 | 1.0102 | 0.51042 | 1.0102 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [MEUR/MW_h] | 0.56359 | 0.56359 | 0.48915 | 0.48915 | 0.48915 | 0.40408 | 0.80816 | 0.40408 | 0.80816 | A | [1, 14, 15]
| Nominal investment (grid connection) [MEUR/MW_e] | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0.10634 | 0.010634 | 0.10634 | J | [1, 14, 15]
| Nominal investment (installation) [MEUR/MW_h] | 0.1276 | 0.1276 | 0.10634 | 0.10634 | 0.10634 | 0.095704 | 0.10634 | 0.095704 | 0.10634 | A | [1, 14, 15]
| Variable O&M (*total) [EUR/MWh_h] | 1.7971 | 1.7971 | 2.1374 | 2.2224 | 1.7971 | 1.2654 | 2.3288 | 1.7971 | 2.8392 |  | [1, 14, 15]
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [D, M] | [1, 14, 15]
| Variable O&M (other O&M) [EUR/MWh_h] | 1.7971 | 1.7971 | 2.1374 | 2.2224 | 1.7971 | 1.2654 | 2.3288 | 1.7971 | 2.8392 | L | [1, 14, 15]
| Fixed O&M (*total) [EUR/MW_h/y] | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 1063.3727 | 3190.1182 | 1063.3727 | 5316.8636 | L | [1, 14, 15]
| Startup cost [EUR/MW_h/startup] | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 5.3169 | 21.2675 | 2.1267 | 21.2675 | N | 15
Technology-specific data
Notes:
A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, seawater 20 MW
Technology |  | Heat pump, sea water - heat pump - electricity - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 20 | 20 | 20 | 20 | 20 | 10 | 50 | 10 | 100
| Heat efficiency (net, annual average) [] | 370% | 370% | 370% | 380% | 380% | 360% | 380% | 370% | 390% | [A, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 340% | 340% | 340% | 350% | 350% | 330% | 350% | 340% | 360% | [A, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 0.7 | 1.5 | 0.5 | 1.5 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 | O | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | G | [9, 14, 15]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 2 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.51042 | 0.51042 | 0.40408 | 0.40408 | 0.40408 | 0.30838 | 1.0634 | 0.30838 | 1.0634 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [MEUR/MW_h] | 0.42535 | 0.42535 | 0.34028 | 0.34028 | 0.34028 | 0.25521 | 0.90387 | 0.25521 | 0.90387 | A | [1, 14, 15]
| Nominal investment (grid connection) [MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0.10634 | 0 | 0.10634 | J | [1, 14, 15]
| Nominal investment (installation) [MEUR/MW_h] | 0.074436 | 0.074436 | 0.063802 | 0.063802 | 0.063802 | 0.042535 | 0.053169 | 0.042535 | 0.053169 | A | [1, 14, 15]
| Variable O&M (*total) [EUR/MWh_h] | 1.2654 | 1.2654 | 1.6057 | 1.6908 | 1.7758 | 1.2654 | 1.7971 | 1.5632 | 1.2654 |  | [1, 14, 15]
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | [1, 14, 15]
| Variable O&M (other O&M) [EUR/MWh_h] | 1.2654 | 1.2654 | 1.6057 | 1.6908 | 1.7758 | 1.2654 | 1.7971 | 1.5632 | 1.2654 | L | [1, 14, 15]
| Fixed O&M (*total) [EUR/MW_h/y] | 4253.4909 | 4253.4909 | 4253.4909 | 4253.4909 | 4253.4909 | 2126.7454 | 5316.8636 | 2126.7454 | 5316.8636 | L | [1, 14, 15]
| Startup cost [EUR/MW_h/startup] | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 10.6337 | 5.3169 | 21.2675 | 2.1267 | 21.2675 | N | 15
Technology-specific data
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
B. Total efficiency, net (%), name plate is at a sea water temperature of 4 °C and district heating temperatures of 40 °C return and 80 °C forward.
C. Annual average is at varying sea water temperatures and district heating temperatures of 40 °C return and 80 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected to existing power stations
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. Regards heat pumps that are installed at existing power plants utilizing existing infra structure such as power supply, seawater intake, DH pipes etc. For stand alone plants it is estimated that the total investment is around the upper uncertainty in the table.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Absorption heat pump, DH
Technology |  | Absorption heat pump - heat pump - heat - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 12 | 12 | 12 | 12 | 12 | 20 | 12 | 30 | [A, A1] | 13
| Heat efficiency (net, annual average) [] | 170% | 171% | 173% | 175% | 170% | 180% | 170% | 180% | B | 4
Heat efficiency (net, name plate) []
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 3% | 1% | 3% | E | 3
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 1% | 0% | 1% | C
| Planned outage [weeks per year] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 15 | 30 | 15 | 30 |  | 3
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7
| Space requirement [1000 m2/MW_h] | 0.01 | 0.01 | 0 | 0 | 0 | 0.01 | 0 | 0.01
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 2 | 0.25 | 2
Environment
| SO2 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.63802 | 0.59549 | 0.54232 | 0.48915 | 0.42535 | 0.8507 | 0.42535 | 0.8507 | [A, A1] | 3
| Nominal investment (equipment) [MEUR/MW_h] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 31.9012 | 74.4361 | 31.9012 | 74.4361 | 0 | 3
| Nominal investment (installation) [MEUR/MW_h] | 53.1686 | 53.1686 | 53.1686 | 53.1686 | 31.9012 | 74.4361 | 31.9012 | 74.4361 | 0 | 3
| Variable O&M (*total) [EUR/MWh_h] | 0.95704 | 1.0421 | 1.3292 | 1.5206 | 1.0634 | 2.6584 | 1.4887 | 0.31901 | 0
| Variable O&M (electricity cost) [EUR/MWh_h] | 0.63802 | 0.74436 | 1.0634 | 1.276 | 0.74436 | 2.2331 | 1.276 | 0 | E
| Variable O&M (other O&M) [EUR/MWh_h] | 0.31901 | 0.29774 | 0.26584 | 0.24458 | 0.31901 | 0.42535 | 0.21267 | 0.31901 | 0 | 3
| Fixed O&M (*total) [EUR/MW_h/y] | 2126.7454 | 2126.7454 | 2126.7454 | 2126.7454 | 1063.3727 | 3190.1182 | 1063.3727 | 3190.1182 | 0 | 3
Technology-specific data
Notes:
A. The heat pump itself only represents a small part of the total investment. Depending on size the heat pump typically represents 0.2 MEUR per. MW heating (excluding drive energy).
A1. Capacity is excluding drive energy.
B. The heat is assumed delivered at 80 °C in 2015 and 60 °C in 2050
C. May vary depending on availability of heat source
D. May vary depending on specific type, heat source etc.
E. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014, see http://www.planenergi.dk/varmepumper/
4. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, 2013
13. Scandinavian Energy Group, 2015

## 40 co2. hp, seawater 50-100 MW
Technology |  | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 65 | 65 | 65 | 65 | 65 | 30 | 150 | 30 | 300 | A,B, M | 1
| Heat efficiency (net, annual average) [] | 301% | 301% | 301% | 311% | 311% | 290% | 310% | 300% | 320% | C, D, F, M, V | 1
| Heat efficiency (net, name plate) [] | 320% | 320% | 320% | 330% | 330% | 310% | 330% | 320% | 340% | C, D, F, M | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | E, F, M | 1
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% | M | 1
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 | M | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 | G,M | 1
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 1.5 | 3 | 1 | 3 | H, I, M | 1
| Space requirement [1000 m2/MW_h] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 | M | 1
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 65% | 65% | 65% | 65% | 65% | 65% | 100% | 65% | 100% | J, K, M | 1
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | J, K, M | 1
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | K, L, M | 1
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.75 | 0.25 | 0.75 | K, N, M | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 1 | 0.25 | 1 | K, O, M | 1
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.94 | 0.94 | 0.89 | 0.84 | 0.8 | 0.79 | 1.4 | 0.65 | 1.4 | A, M, R | 1
| Nominal investment (seawater system) [MEUR/MW_h] | 0.2 | 0.2 | 0.19 | 0.18 | 0.17 | 0.15 | 0.3 | 0.14 | 0.3 | M, R | 1
| Nominal investment (equipment) [MEUR/MW_h] | 0.57 | 0.57 | 0.54 | 0.52 | 0.49 | 0.45 | 0.86 | 0.4 | 0.86 | M, R | 1
| Nominal investment (installation) [MEUR/MW_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M, R | 1
| Nominal investment (other) [MEUR/MW_h] | 0.16 | 0.16 | 0.15 | 0.14 | 0.14 | 0.13 | 0.24 | 0.11 | 0.24 | M, R | 1
| Variable O&M (*total) [EUR/MWh_h] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.5 | 1.98 | 0.5 | 1.98 | M, R, S | 1
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M, P | 1
| Variable O&M (other O&M) [EUR/MWh_h] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.5 | 1.98 | 0.5 | 1.98 | M, R, S | 1
| Fixed O&M (*total) [EUR/MW_h/y] | 2047.35 | 2047.35 | 2047.35 | 2047.35 | 2047.35 | 1485.15 | 2970.3 | 1485.15 | 2970.3 | M, R | 1
| Startup cost [EUR/MW_h/startup] | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 2.97 | 14.85 | 2.97 | 14.85 | M, Q | 1
Technology-specific data
| Nominal investment (grid connection fee) [MEUR/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.01 | 0.08 | 0.03 | 0.08 | M, T | 1
| Nominal investment (heatpump building) [MEUR/MW_h] | 0.11 | 0.11 | 0.1 | 0.1 | 0.09 | 0.09 | 0.16 | 0.05 | 0.16 | M, T | 1
| Nominal investment (seawater connection) [MEUR/MW_h] | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.07 | 0.13 | 0.04 | 0.13 | M, T | 1
| Nominal investment (seawater intake) [MEUR/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.03 | 0.08 | M, T | 1
| Nominal investment (seawater piping) [EUR/m] | 1663.47 | 1663.47 | 1580.3 | 1497.13 | 1413.95 | 1413.95 | 2495.21 | 831.74 | 2495.21 | M, T | 1
Notes:
A. Design temperatures are 4 °C seawater and DH temperatues of 70/33 °C.
B. 45 MW at 1 °C seawater, 64,5 at 4 °C seawater (the design temperature), and 68,4 MW at 14 °C seawater.
C. Actual development within COP optimization and reduced investment cost depend on the development in fuel and electricity prices.
D. Name plate efficiency is at 4 °C seawater temperature and DH temperatures are 70/33 °C. Total efficiency is in the range of 2,4 to 3,6 depending on the temperature of the seawater and DH. The plant is not in use in the summer period, otherwise, the efficiency could have been even higher.
E. The primary auxililary electricity consumption is related to the seawater pumps.
F. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M.
G. Tecnical lifetime is calculated with an outage time of 3 month per year.
H. Does not include tendering and regulatory approvals.
I. The development within construction time will depend on future production figures and standardization of plants.
J. Note that this is only valid for upregulation (i.e. load increase of the heat pump). Downregulation (i.e. load reduction on the heat pump) is at a lower rate, however, this can be compesated by other units in the portfolio.
K. CO2 heat pumps regulate a lot faster than e.g. ammonia. The regulation ability will depend on the future markets for regulation services.
L. This is the continous minimum load with only 1 of 2 HP's enabled.
M. All inputs are based on a single case, DIN Forsyning Heat Pump in Esbjerg.
N. The warm start-up time is guaranteed to take 0,5 hours but it is, however, expected to take 0,2 hours.
O. Cold start-up time includes starting a heat pump where stand by heating has not been applied.
P. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M. DH distribution system is not included.
Q. 1/4 MWh-heat per MW is lost during startup
R. The forecast for future prices is an estimate since this is the first CO2 heat pump plant in this size.
S. The CO2 heat pumps are made with magnetic barrings and are oilfree, therefore the O&M are lower compared to traditional heat pumps
T. The price is also included in nominal investment (equipment)
V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Interview with DIN Forsyning

## 41 Electric boiler, small
Technology |  | Electric boiler - boiler - electricity - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2030 | 2030 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 2 | 2 | 2 | 2 | 1 | 5 |  |  | 1 | 5
| Heat efficiency (net, name plate) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Heat efficiency (net, annual average) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% |  |  | 0.1% | 0.5%
| Forced outage [] | 1% | 1% | 1% | 1% | 0.5% | 1% |  |  | 0.5% | 1%
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  | 0.2 | 0.2
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 |  |  | 25 | 25
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 |  |  | 0.5 | 1
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
Minimum load (of full load) [] | bar: ctrl to upper; lower to upper
| Warm start-up time [hours] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01
| Cold start-up time [hours] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 |  |  | 0.08 | 0.08
Environment
SO2 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.15951 | 0.15951 | 0.14887 | 0.13824 | 0.10634 | 0.26584 | 0 | 0 | 0.10634 | 0.25
| Nominal investment (equipment) [MEUR/MW_h] | 0.1276 | 0.1276 | 0.11697 | 0.10634 | 0.08507 | 0.21267 | 0 | 0 | 0.08507 | 0.2
| Nominal investment (installation) [MEUR/MW_h] | 0.031901 | 0.031901 | 0.031901 | 0.031901 | 0.021267 | 0.053169 | 0 | 0 | 0.021267 | 0.05
| Variable O&M (*total) [EUR/MWh_h] | 0.8507 | 0.95704 | 1.0634 | 1.0634 | 0.53169 | 0.95704 | 0 | 0 | 0.53169 | 1
| Variable O&M (electricity cost) [EUR/MWh_h] | 0.31901 | 0.31901 | 0.53169 | 0.63802 | 0.10634 | 0.31901 | 0 | 0 | 0.10634 | 0.6
| Variable O&M (other O&M) [EUR/MWh_h] | 0.53169 | 0.53169 | 0.53169 | 0.42535 | 0.42535 | 0.53169 | 0 | 0 | 0.31901 | 0.5
| Fixed O&M (*total) [EUR/MW_h/y] | 1169.71 | 1137.8088 | 1084.6402 | 978.3029 | 1063.3727 | 1169.71 | 0 | 0 | 957.0354 | 1000
Technology-specific data
| Startup cost [EUR/MW_h/startup] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Notes:
A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
D. The installation costs include costs for electrical integration & grid connection fees.
E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Tjæreborg Industri, 2016
2. Parat, unknown date, Brochure High Voltage Electrode Boiler, available at http://parat.no/media/201154/Electrode-Boiler-web.pdf

## 41 Electric boiler, large
Technology |  | Electric boiler - boiler - electricity - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2030 | 2030 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 15 | 15 | 15 | 15 | 5 | 25 |  |  | 5 | 25
| Heat efficiency (net, name plate) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Heat efficiency (net, annual average) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% |  |  | 0.1% | 0.5%
| Forced outage [] | 1% | 1% | 1% | 1% | 0.5% | 1% |  |  | 0.5% | 1%
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  | 0.2 | 0.2
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 |  |  | 25 | 25
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 |  |  | 0.5 | 1
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
Minimum load (of full load) [] | bar: ctrl to upper; lower to upper
| Warm start-up time [hours] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01
| Cold start-up time [hours] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 |  |  | 0.08 | 0.08
Environment
SO2 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.074436 | 0.074436 | 0.063802 | 0.063802 | 0.021267 | 0.18077 | 0 | 0 | 0.021267 | 0.17
| Nominal investment (equipment) [MEUR/MW_h] | 0.063802 | 0.063802 | 0.053169 | 0.053169 | 0.021267 | 0.14887 | 0 | 0 | 0.021267 | 0.14
| Nominal investment (installation) [MEUR/MW_h] | 0.010634 | 0.010634 | 0.010634 | 0.010634 | 0 | 0.031901 | 0 | 0 | 0 | 0.03
| Variable O&M (*total) [EUR/MWh_h] | 0.8507 | 0.95704 | 1.0634 | 1.0634 | 0.53169 | 0.95704 | 0 | 0 | 0.53169 | 1
| Variable O&M (electricity cost) [EUR/MWh_h] | 0.31901 | 0.31901 | 0.53169 | 0.63802 | 0.10634 | 0.31901 | 0 | 0 | 0.10634 | 0.6
| Variable O&M (other O&M) [EUR/MWh_h] | 0.53169 | 0.53169 | 0.53169 | 0.42535 | 0.42535 | 0.53169 | 0 | 0 | 0.31901 | 0.5
| Fixed O&M (*total) [EUR/MW_h/y] | 1169.71 | 1137.8088 | 1084.6402 | 978.3029 | 1063.3727 | 1169.71 | 0 | 0 | 957.0354 | 1000
Technology-specific data
| Startup cost [EUR/MW_h/startup] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Notes:
A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
D. The installation costs include costs for electrical integration & grid connection fees.
E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Tjæreborg Industri, 2016
2. Parat, unknown date, Brochure High Voltage Electrode Boiler, available at http://parat.no/media/201154/Electrode-Boiler-web.pdf

## 44 Natural Gas DH Only
Technology |  | Gas boiler - boiler - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | lower: 0.5; upper: 10; lower: 0.5; upper: 10
| Heat efficiency (net, annual average) [] | 103% | 103% | 104% | 104% | 93% | 105% | 94% | 106% | B | [1, 3]
| Heat efficiency (net, name plate) [] | 105% | 105% | 106% | 106% | 95% | 107% | 96% | 108% | A | [1, 2, 3]
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.15% | 0.14% | 0.12% | 0.1% | 0.13% | 0.2% | 0.08% | 0.15% | L | 1
| Forced outage [] | 1% | 1% | 1% | 1% | 0.08% | 2% | 0.08% | 2% |  | 3
| Planned outage [weeks per year] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 | F | 3
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | K | 3
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 | F | 9
| Space requirement [1000 m2/MW_h] | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.01 | E | 2
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% |  | 9
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.08 | 0.15 | 0.08 | 0.15 | D | 9
| Cold start-up time [hours] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 | D | 9
Environment
| SO2 [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0 | 0.3 | H | 1
| NOX [g/GJ_i] | 10 | 9 | 7 | 6 | 8 | 60 | 5 | 30 |  | [1, 2]
| CH4 [g/GJ_i] | 3 | 3 | 2 | 2 | 2 | 6 | 2 | 6 |  | [1, 2]
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 |  |  |  |  | I | 7
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.063802 | 0.063802 | 0.053169 | 0.053169 | 0.042535 | 0.26584 | 0.042535 | 0.26584 | J | [2, 3]
| Nominal investment (equipment) [MEUR/MW_h] | 0.042535 | 0.042535 | 0.031901 | 0.031901 | 0.031901 | 0.15951 | 0.031901 | 0.15951 | 0 | [2, 3]
| Nominal investment (installation) [MEUR/MW_h] | 0.021267 | 0.021267 | 0.021267 | 0.021267 | 0.010634 | 0.10634 | 0.010634 | 0.10634 | 0 | [2, 3]
| Variable O&M (*total) [EUR/MWh_h] | 1.1697 | 1.1697 | 1.0634 | 1.0634 | 0.63802 | 2.2331 | 0.63802 | 2.3394 | 0
| Variable O&M (electricity cost) [EUR/MWh_h] | 0.10634 | 0.10634 | 0.10634 | 0.10634 | 0.10634 | 0.10634 | 0.10634 | 0.21267 | L
| Variable O&M (other O&M) [EUR/MWh_h] | 1.0634 | 1.0634 | 0.95704 | 0.95704 | 0.53169 | 2.1267 | 0.53169 | 2.1267 | 0 | [8, 9]
| Fixed O&M (*total) [EUR/MW_h/y] | 2126.7454 | 2073.5768 | 2020.4082 | 1807.7336 | 1063.3727 | 2658.4318 | 1063.3727 | 2658.4318 | F
Technology-specific data
Notes:
A. Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
B. Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
C. Not Relevant for heat-only technologies
D. Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
E. Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
F. DGC Estimate
G. Ultra Low NOx burners can reach a level of 5 g/GJ
H. Fuel dependent , not tecchnology dependent
I. No data available
J. The average numbers are for a 2- 3 MW boiler installation
K. Technical lifetime often exceeds 25 years
L. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. DGC efficiency and emission test reports from district heating boilers, 2014
2. Burner and boiler manufacturer informations, 2015
3. Danish District Heating Association, data from a 2012 survey for the report
7. National Environmental Research Institute, Denmark 2009
8. Elsam/Elkraft update "Teknologidata for el- og varmeproduktionsanlæg", 1997
9. DGC calculations, estimates

## 45.1.a Geothermal DH, 1200m, E
Technology |  | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 11.42 | 11.37 | 11.33 | 11.24 | 11.2 | 19.28 | 4.28 | 19.28 | 4.28 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 460.3% | 467.2% | 474% | 487.6% | 494.2% | 530.9% | 405.9% | 575.5% | 431.6% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.121% | 4.138% | 4.154% | 4.185% | 4.199% | 1.647% | 7.423% | 1.647% | 7.423% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 2.8817 | 2.8179 | 2.6584 | 2.5946 | 2.5308 | 1.7333 | 4.3173 | 1.6163 | 3.9983 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [MEUR/MW_h] | 1.6376 | 1.5844 | 1.5419 | 1.4887 | 1.4462 | 0.9145 | 2.4564 | 0.82943 | 2.2331 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [MEUR/MW_h] | 0.71246 | 0.71246 | 0.60612 | 0.60612 | 0.60612 | 0.49979 | 1.0102 | 0.49979 | 0.98894 | [J, K]
| Nominal investment (installation) [MEUR/MW_h] | 0.54232 | 0.53169 | 0.51042 | 0.49979 | 0.47852 | 0.31901 | 0.84006 | 0.28711 | 0.76563 |  | [2, 4]
| Variable O&M (*total) [EUR/MWh_h] | 6.0612 | 6.0719 | 6.5185 | 6.6461 | 6.2314 | 5.4126 | 6.4759 | 6.1144 | 7.0608 | FJ | 2
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 6.0612 | 6.0719 | 6.5185 | 6.6461 | 6.2314 | 5.4126 | 6.4759 | 6.1144 | 7.0608 | F
| Fixed O&M (*total) [EUR/MW_h/y] | 24032.2234 | 23287.8625 | 22649.8389 | 21905.478 | 21161.1171 | 23287.8625 | 23287.8625 | 21161.1171 | 21161.1171 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 568% | 579.1% | 590.3% | 612.5% | 623.7% | 579.1% | 579.1% | 623.7% | 623.7% | [A, N]
| Heat generation from heat pumps [MW_h] | 2.01 | 1.96 | 1.92 | 1.84 | 1.8 | 3.31 | 0.74 | 3.03 | 0.67 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.53 | 15.88 | 3.53 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. No part of the geothermal heat is transferred directly to DH water, all is used as source for the heat pump Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1800 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.1.b Geothermal DH, 2000m, E
Technology |  | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 13.14 | 13.11 | 13.09 | 13.05 | 13.03 | 22.18 | 4.93 | 22.18 | 4.93 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 844.4% | 855.3% | 866.1% | 887% | 897.2% | 1124% | 650.4% | 1208% | 677.4% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 6.501% | 6.513% | 6.523% | 6.543% | 6.553% | 3.712% | 9.27% | 3.712% | 9.27% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 3.0625 | 2.9774 | 2.8605 | 2.7754 | 2.6903 | 1.8077 | 4.4024 | 1.6589 | 4.0302 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [MEUR/MW_h] | 2.1055 | 2.0417 | 1.9779 | 1.9247 | 1.8609 | 1.2122 | 3.0093 | 1.0953 | 2.7329 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [MEUR/MW_h] | 0.25521 | 0.25521 | 0.22331 | 0.22331 | 0.21267 | 0.18077 | 0.36155 | 0.18077 | 0.36155 | [J, K]
| Nominal investment (installation) [MEUR/MW_h] | 0.70183 | 0.68056 | 0.65929 | 0.63802 | 0.61676 | 0.41472 | 1.0315 | 0.38281 | 0.93577 |  | [2, 4]
| Variable O&M (*total) [EUR/MWh_h] | 4.8809 | 4.8064 | 4.8809 | 4.849 | 4.615 | 4.5619 | 4.9447 | 4.5831 | 4.9128 | FJ | 2
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 4.8809 | 4.8064 | 4.8809 | 4.849 | 4.615 | 4.5619 | 4.9447 | 4.5831 | 4.9128 | F
| Fixed O&M (*total) [EUR/MW_h/y] | 25414.608 | 24670.2471 | 23925.8862 | 23181.5253 | 22437.1643 | 24670.2471 | 24670.2471 | 22437.1643 | 22437.1643 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 505% | 514.9% | 524.8% | 544.6% | 554.5% | 514.9% | 514.9% | 554.5% | 554.5% | [A, N]
| Heat generation from heat pumps [MW_h] | 0.95 | 0.92 | 0.9 | 0.86 | 0.84 | 1.56 | 0.35 | 1.43 | 0.32 | A | 1
| Heat generation from geothermal ressource [MW_h] | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.58 | 4.57 | 20.58 | 4.57 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 2000 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.2.a Geothermal DH, 1200m, A
Technology |  | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 22.66 | 22.47 | 22.3 | 22.12 | 21.95 | 38.56 | 8.56 | 38.56 | 8.56 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 165.1% | 166% | 166.9% | 167.8% | 168.7% | 172.3% | 164.4% | 179.4% | 170.9% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.076% | 2.093% | 2.11% | 2.127% | 2.143% | 0.8237% | 3.701% | 0.8237% | 3.701% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 1.3398 | 1.3079 | 1.2654 | 1.2229 | 1.191 | 0.7869 | 1.9991 | 0.73373 | 1.8503 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [MEUR/MW_h] | 0.8188 | 0.79753 | 0.77626 | 0.75499 | 0.72309 | 0.45725 | 1.2335 | 0.41472 | 1.1165 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [MEUR/MW_h] | 0.24458 | 0.23394 | 0.23394 | 0.22331 | 0.21267 | 0.17014 | 0.35091 | 0.17014 | 0.35091 | [J, K]
| Nominal investment (installation) [MEUR/MW_h] | 0.27648 | 0.26584 | 0.25521 | 0.25521 | 0.24458 | 0.15951 | 0.42535 | 0.13824 | 0.38281 |  | [2, 4]
| Variable O&M (*total) [EUR/MWh_h] | 2.2118 | 2.2437 | 2.2756 | 2.265 | 2.2437 | 2.2012 | 2.2012 | 2.1586 | 2.1586 | FJ | 2
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 2.2118 | 2.2437 | 2.2756 | 2.265 | 2.2437 | 2.2012 | 2.2012 | 2.1586 | 2.1586 | F
| Fixed O&M (*total) [EUR/MW_h/y] | 11803.4372 | 11484.4254 | 11165.4135 | 10740.0645 | 10421.0526 | 11484.4254 | 11484.4254 | 10421.0526 | 10421.0526 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 171% | 172% | 173% | 174% | 175% | 172% | 172% | 175% | 175% | [A, N]
| Heat generation from heat pumps [MW_h] | 13.25 | 13.07 | 12.89 | 12.71 | 12.54 | 22.06 | 4.89 | 21.17 | 4.69 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.52 | 15.88 | 3.52 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. No part of the geothermal heat is transferred directly to DH water. 100% heat source for the heat pump. Heat pump according to Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1800 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.2.b Geothermal DH, 2000m, A
Technology |  | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 17.58 | 17.51 | 17.44 | 17.37 | 17.3 | 29.84 | 6.62 | 29.84 | 6.62 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 292.9% | 295.3% | 297.7% | 300.1% | 302.6% | 316.9% | 274.8% | 329.5% | 284.2% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.857% | 4.877% | 4.898% | 4.918% | 4.937% | 2.761% | 6.903% | 2.761% | 6.903% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 2.2224 | 2.1586 | 2.0948 | 2.031 | 1.9672 | 1.3398 | 3.0519 | 1.2122 | 2.7648 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [MEUR/MW_h] | 1.5738 | 1.5313 | 1.4781 | 1.4356 | 1.393 | 0.87197 | 2.2437 | 0.7869 | 2.031 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [MEUR/MW_h] | 0.1276 | 0.1276 | 0.11697 | 0.11697 | 0.11697 | 0.17014 | 0.042535 | 0.14887 | 0.031901 | [J, K]
| Nominal investment (installation) [MEUR/MW_h] | 0.52105 | 0.51042 | 0.48915 | 0.47852 | 0.46788 | 0.29774 | 0.76563 | 0.27648 | 0.70183 |  | [2, 4]
| Variable O&M (*total) [EUR/MWh_h] | 3.1795 | 3.1476 | 3.105 | 3.0412 | 2.9774 | 3.1157 | 3.1157 | 2.9136 | 2.9136 | FJ | 2
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 3.1795 | 3.1476 | 3.105 | 3.0412 | 2.9774 | 3.1157 | 3.1157 | 2.9136 | 2.9136 | F
| Fixed O&M (*total) [EUR/MW_h/y] | 18396.348 | 17864.6617 | 17332.9753 | 16801.2889 | 16269.6026 | 17864.6617 | 17864.6617 | 16269.6026 | 16269.6026 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 171% | 172% | 173% | 174% | 175% | 172% | 172% | 175% | 175% | [A, N]
| Heat generation from heat pumps [MW_h] | 5.39 | 5.32 | 5.25 | 5.18 | 5.11 | 9.01 | 2 | 8.65 | 1.92 | A | 1
| Heat generation from geothermal ressource [MW_h] | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.6 | 4.57 | 20.6 | 4.57 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump according to Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.3.a Geoth. DH, 1200m, E (LT)
Technology |  | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10.93 | 10.9 | 10.86 | 10.8 | 10.77 | 18.45 | 4.1 | 18.45 | 4.1 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 548.1% | 556.1% | 564% | 579.6% | 587.3% | 651.7% | 467.8% | 704.3% | 494.3% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.304% | 4.318% | 4.331% | 4.356% | 4.368% | 1.721% | 7.749% | 1.721% | 7.749% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 2.8711 | 2.8073 | 2.6478 | 2.584 | 2.5202 | 1.7014 | 4.296 | 1.5738 | 3.977 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [MEUR/MW_h] | 1.7014 | 1.6589 | 1.6057 | 1.5525 | 1.51 | 0.9464 | 2.5627 | 0.86133 | 2.3394 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [MEUR/MW_h] | 0.59549 | 0.59549 | 0.51042 | 0.51042 | 0.51042 | 0.42535 | 0.8507 | 0.41472 | 0.84006 | [J, K]
| Nominal investment (installation) [MEUR/MW_h] | 0.56359 | 0.55295 | 0.53169 | 0.52105 | 0.49979 | 0.32965 | 0.8826 | 0.29774 | 0.79753 |  | [2, 4]
| Variable O&M (*total) [EUR/MWh_h] | 5.806 | 5.7954 | 6.1463 | 6.2314 | 5.8592 | 5.2424 | 6.1357 | 5.7741 | 6.5716 | FJ | 2
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 5.806 | 5.7954 | 6.1463 | 6.2314 | 5.8592 | 5.2424 | 6.1357 | 5.7741 | 6.5716 | F
| Fixed O&M (*total) [EUR/MW_h/y] | 24670.2471 | 23925.8862 | 23181.5253 | 22437.1643 | 21799.1407 | 23925.8862 | 23925.8862 | 21799.1407 | 21799.1407 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 603% | 614.8% | 626.6% | 650.3% | 662.1% | 614.8% | 614.8% | 662.1% | 662.1% | [A, N]
| Heat generation from heat pumps [MW_h] | 1.52 | 1.49 | 1.46 | 1.39 | 1.36 | 2.51 | 0.56 | 2.3 | 0.51 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.53 | 15.88 | 3.53 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 19% of geothermal heat can be exchanged directly, leaving 79 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.3.b Geoth DH, 2000m, E (LT)
Technology |  | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 12.65 | 12.64 | 12.63 | 12.61 | 12.6 | 21.35 | 4.73 | 21.35 | 4.73 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 1185% | 1196% | 1207% | 1228% | 1237% | 1830% | 816.9% | 1937% | 837.6% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 6.75% | 6.755% | 6.761% | 6.771% | 6.776% | 3.856% | 9.662% | 3.856% | 9.662% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: -
Secondary regulation (of full load, per minute) [] | bar: -
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 3.0625 | 2.9668 | 2.8605 | 2.7754 | 2.6903 | 1.7333 | 4.413 | 1.5844 | 4.0302 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [MEUR/MW_h] | 2.1905 | 2.1267 | 2.0629 | 1.9885 | 1.9247 | 1.2122 | 3.1369 | 1.1059 | 2.8498 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [MEUR/MW_h] | 0.13824 | 0.13824 | 0.11697 | 0.11697 | 0.11697 | 0.10634 | 0.20204 | 0.095704 | 0.20204 | [J, K]
| Nominal investment (installation) [MEUR/MW_h] | 0.73373 | 0.71246 | 0.69119 | 0.65929 | 0.63802 | 0.41472 | 1.074 | 0.38281 | 0.9783 |  | [2, 4]
| Variable O&M (*total) [EUR/MWh_h] | 4.615 | 4.5193 | 4.5087 | 4.4236 | 4.2429 | 4.3811 | 4.6044 | 4.2322 | 4.4236 | FJ | 2
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 4.615 | 4.5193 | 4.5087 | 4.4236 | 4.2429 | 4.3811 | 4.6044 | 4.2322 | 4.4236 | F
| Fixed O&M (*total) [EUR/MW_h/y] | 26052.6316 | 25308.2707 | 24563.9098 | 23713.2116 | 22968.8507 | 25308.2707 | 25308.2707 | 22968.8507 | 22968.8507 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 557% | 567.9% | 578.8% | 600.7% | 611.6% | 567.9% | 567.9% | 611.6% | 611.6% | [A, N]
| Heat generation from heat pumps [MW_h] | 0.46 | 0.45 | 0.44 | 0.42 | 0.41 | 0.76 | 0.17 | 0.69 | 0.15 | A | 1
| Heat generation from geothermal ressource [MW_h] | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.58 | 4.57 | 20.58 | 4.57 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 83% of geothermal heat can be exchanged directly, leaving 17 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary.
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 80/40 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.4 Geothermal DH, E lar scale
Technology |  | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 121 | 120.77 | 120.38 | 119.67 | 119.32 | 120.77 | 120.77 | 119.32 | 119.32 | I,A | 1, 2
| Heat efficiency (net, annual average) [] | 374% | 374% | 374% | 378.2% | 385.3% | 374% | 374% | 385.3% | 385.3% | A,G
Heat efficiency (net, name plate) []
| Auxiliary Electricity consumption (share of heat gen.) [] | 9.626% | 9.626% | 9.626% | 9.5% | 9.4% | 9.626% | 9.626% | 9.626% | 9.4% | B | 2, 3; 4
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | 2; 5
| Warm start-up time [hours] | 4 | 4 | 4 | 4 | 4 | 3 | 5 | 3 | 5
| Cold start-up time [hours] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 1.34 | 1.3 | 1.27 | 1.23 | 1.2 | 1.11 | 1.5 | 1.02 | 1.38 | C,K | 2, 4, 7
| Nominal investment (heatpump, installation incl) [MEUR/MW_h] | 0.27 | 0.26 | 0.25 | 0.25 | 0.24 | 0.22 | 0.3 | 0.2 | 0.28 | J | 2, 4
| Nominal investment (surface installation excl. heatpump) [MEUR/MW_h] | 0.4 | 0.39 | 0.38 | 0.37 | 0.36 | 0.33 | 0.45 | 0.31 | 0.41 | J
| Nominal investment (wells and down hole eq.) [MEUR/MW_h] | 0.67 | 0.65 | 0.63 | 0.62 | 0.6 | 0.55 | 0.75 | 0.51 | 0.69 |  | 2, 4
| Variable O&M (*total) [EUR/MWh_h] | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | F,J | 2, 4
| Variable O&M (electricity cost) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [EUR/MWh_h] | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 3 | 2.02 | 3 | F | 2, 4
| Fixed O&M (*total) [EUR/MW_h/y] | 18791.95 | 18255.03 | 17718.12 | 17104.51 | 16567.59 | 15516.78 | 20993.29 | 14082.45 | 19052.73 | E,J | 2, 4
Startup cost [EUR/MW_h/startup]
Technology-specific data
| Nominal Abandonment Cost (ABEX) [MEUR/MW_h] | 0.1 | 0.1 | 0.1 | 0.09 | 0.09 | 0.08 | 0.11 | 0.08 | 0.1 | O | 2, 7
| Number of injection wells | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | L, N | 2
| Number of production wells | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 6 | 12 | L | 2
| Heat pump SCOP (net, annual average) [] | 377% | 381.2% | 388.4% | 402.5% | 409.7% | 381% | 381% | 410% | 410% | A, N
| Heat generation from heat pumps [MW_h] | 21 | 20.77 | 20.38 | 19.67 | 19.32 | 17.65 | 23.88 | 16.43 | 22.22 | A | 2
| Heat generation from geothermal ressource [MW_h] | 100 | 100 | 100 | 100 | 100 | 85 | 115 | 85 | 115 | I,A,L,N | 2
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1, 2
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump. 44% of geothermal heat can be exchanged directly, leaving 56% as heat source for the heat pump. Heat pump COP based on specific case according to [2]. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Based on large scale effects. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey etc. and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 2000 EUR/m is assumed.
D. The requirement is per facility. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Including maintenance of filters and wells (chemical treatment). Does not include drilling of replacement wells.
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electrical heat pumps may provide some of the regulation though, e.g. in connection with an energy storage to allow for use of the heating when required.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Heat pump nominal investment costs including installation and integration with geothermal plant, excl. Building integration, electrical supply and district heating connection
K. The basis of the specific investment is the heat generation capacity for one unit including heat pumps but excluding ABEX.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 65/10 (°C source/return). Temperature of DH water is (°C source/return) 90/45 (500 h), 85/40 (1500 h) and 80/40 (rest of estimated hours)
O. Abandonment Cost (ABEX) accounts for approx. 7,5 % of total nominal investment [2]
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Input from Innargi Nov 2021 - One case scenario
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 46 Solar District Heating
Technology |  | Solar DH - renewable heat - solar - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat efficiency (net, annual average) [] | 43% | 45% | 48% | 49.95% | 42% | 49% | 46% | 54% | P
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.3% | 0.3% | 0.3% | 0.3% | 0.2% | 0.4% | 0.2% | 0.4%
| Forced outage [] | 0.5% | 0.5% | 0.5% | 0.5% | 0% | 1% | 0% | 1% | K
| Technical lifetime [years] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | I | 17
| Construction time [years] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Space requirement [1000 m2/MWh_h/y] | 6.7 | 6.3 | 6 | 5.7 | 6 | 6.7 | 5.5 | 6 | J
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) [] | bar: -
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (*total) [MEUR/MW_h] | 0.32965 | 0.32965 | 0.31901 | 0.29774 | 0.30838 | 0.34028 | 0.27648 | 0.32965 | [C, E, H, N, S] | [16, 18]
| Nominal investment (equipment) [MEUR/MW_h] | 0.24458 | 0.24458 | 0.23394 | 0.22331 | 0.23394 | 0.24458 | 0.20204 | 0.23394 | O
| Nominal investment (installation) [MEUR/MW_h] | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.031901 | 0.042535 | O
| Nominal investment (diurnal heat storage) [MEUR/MW_h] | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.031901 | 0.053169 | 0.031901 | 0.053169 | [D, M]
| Variable O&M (*total) [EUR/MWh_h] | 0.20204 | 0.22331 | 0.31901 | 0.37218 | 0.14887 | 0.29774 | 0.24458 | 0.49979 | 0
| Variable O&M (electricity cost) [EUR/MWh_h] | 0.20204 | 0.22331 | 0.31901 | 0.37218 | 0.14887 | 0.29774 | 0.24458 | 0.49979 | R
| Variable O&M (other O&M) [EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [EUR/MW_h/y] | 61.5267 | 64.6637 | 60.4102 | 63.494 | 60.272 | 68.3642 | 58.2516 | 60.4102 | B
Technology-specific data
| Nominal investment (diurnal heat storage) [EUR/MWh_h/y] | 63.8024 | 60.6122 | 57.4221 | 55.2954 | 43.5983 | 79.753 | 39.3448 | 72.3093 | [D, M]
| Nominal investment (total solar system excl diurnal heat storage) [EUR/MWh_h/y] | 456.0699 | 420.4469 | 385.0579 | 346.0215 | 394.5538 | 448.9772 | 310.5899 | 385.0579 | [C, H, N]
| Nominal investment (total solar system excl diurnal heat storage, per collector area) [EUR/m2] | 205.2309 | 198.8507 | 191.4071 | 180.7734 | 195.6606 | 202.0408 | 170.1396 | 191.4071 | [G, H, N] | 16
| Fixed O&M (*total, per annual output) [EUR/MWh_h/y] | 0.095704 | 0.095704 | 0.08507 | 0.08507 | 0.08507 | 0.10634 | 0.074436 | 0.08507 | B
| Fixed O&M (*total, per collector area) [EUR/m2/y] | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.042535 | 0.042535 | B
| Typical plant size (collector area) [m2] | 10000 | 13000 | 21000 | 55000 | 10000 | 20000 | 10000 | 100000 | L
| Collector input [MWh_i/m2/y] | 1.05 | 1.05 | 1.05 | 1.05 | 1.01 | 1.08 | 1.01 | 1.08 | Q
| Collector output [MWh_h/m2/y] | 0.45 | 0.47 | 0.5 | 0.52 | 0.45 | 0.5 | 0.5 | 0.55 | A | 4
Notes:
A. The yield is weather dependent and very site-specific, depending much on the temperatures of the district heating network. The quoted yield the average measured output from 40 Danish solar heating plants for 2015.
B. Estimate is 0,2 EUR/MWh heat output in 2015, excluding electricity consumption.
C. Applying the formula 250,000 EUR + 167 EUR/m2 solar panel collector for plants <50.000m2, cf. figures from Note G.
D. Including a diurnal storage is mandatory, 0.2 m3/m2 being a typical average storage size. This figure can vary, dependent on the local conditions and desired solar fraction.
E. Can be combined with seasonal storage, cf. corresponding chapter.
F. Solar thermal plants can be regulated by varying the flow of the heat transfer fluid. The regulation ability is limited by the available heat demand in the heat sink (incl. available storage capacity) and solar radiation.
G. Prices of different plant sizes (Ref. 1): {"5000":{"Price pr. m2 [eur\/m2]":216.0,"Total price [M-eur]":1.08},"10000":{"Price pr. m2 [eur\/m2]":193.33,"Total price [M-eur]":1.93},"20000":{"Price pr. m2 [eur\/m2]":180.0,"Total price [M-eur]":3.6},"50000":{"Price pr. m2 [eur\/m2]":174.67,"Total price [M-eur]":8.73},"100000":{"Price pr. m2 [eur\/m2]":170.0,"Total price [M-eur]":17.0}}
H. Prices include leveling of ground, laying of district heating pipelines in the ground inkl. 50 m of transmission pipeline to the district heating plant, heat exchanger connected to solar panel field and installed with collection tank and expansion with flanges to secondary side, control and electricity works, design and project management, start-up regulation and documentation.
I. The lifetime is minimum 25-30 years, proven in actual plants still in operation. Critical component is the teflon foil, not the material itself, but the application method. The pipes have been improved, designed for the relatively large number of temperature variations, compared to normal district heating pipelines. The fluid is well managed.
J. Space requirement is approximately 3 m2 for each m2 gross collector area. No development of this parameter is expected, since the main reason is to avoid the shadow effect. Minor optimization of the sides of the panels may be obtained, increasing the ratio of aperture/gross area. Other types of solar collectors such as vacuum and CSP (concentrated solar power) may have lower space requirement.
K. The forced outage is very small, therefore in practice close to 0 %. The modular construction makes it possible to maintain sections of the panels. Outage of critical components such as the heat exchanger is very limited.
L. The average plant size increases, but with large variations since both small plants and increasingly larger plants are installed. A 5 % annual increase of the average size is assumed. The plant size is rather dependent on the heat demand in the district heating grid, it is connected to. The collector area is, cf. international standards, stated as gross area.
M. Estimate of cost of tank storage (diurnal storage) is 135 EUR/m3. The required size of the storage differs, but a typical size is 0.1-0.3 m3 storage for each m2 of solar panels, hence a 10,000 m2 solar thermal plant requires 1-3,000 m3 of diurnal storage.
N. Considering a reduction in prices for 2020 / 2020-2030 / 2030-2050 of 0.6 / 0.4 / 0.3 % p.a.
O. The division of cost elements is site- and plant specific. An indicative distribution of costs are; Solar collectors and piping (48%), heat exchanger, pumps etc. (8%), accumulation tank (11%), transmission pipeline (13%), building (2%), control, operation and startup (5%), land purchase, ground works (7%), design, permits, unforeseen (6%). Total for equipment is 85% and for installation is 15% (design, permits, unforeseen, ground works, control and start up), but including accumulation tank and a transmission pipeline.
P. Please refer to www.solvarmedata.dk for display of efficiencies of Danish solar district heating plants. Chose a plant, select "Production and efficiency" and a chart will display the efficiency - typically varying between 20 and 50%.
Q. The solar radiation on the horizontal surface.
R. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
S. The cost per output power is converted from cost per collector area via formula: Power/Area = 0.7 kWth/m2. Note this is an approximation, original figures are stated per area or MWh
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
4. Solar Heating plants in Denmark, Simon Furbo, Bengt Perers and Federico Bava, Department of Civil Engineering, Technical University of Denmark. The projected outputs for 2020, 2030 and 2050 are not from this reference.
16. Arcon-Sunmark, personal communication. The projected costs are not from this reference, but estimated based on two components; the lower specific costs of larger plants in 2015 and increased competition among suppliers and more efficient production of solar panels.
17. "Life expectancy of solar collectors in solar district heating systems", Department of Civil Engineering, Technical University of Denmark, 2009.
18. "Recommendation1: Converting solar thermal collector area into installed capacity (m2 to kWth) ", Solar Heaing and Cooling programme, IEA , 2004.

## 50 Diesel engine farm
Technology |  | Engine, peak plant - back pressure - diesel - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 18; -: [A, B]
| Electrical efficiency (net, annual average) [] | 35% | 35% | 35% | 35% | 33% | 37% |  |  | C
| Electrical efficiency (net, name plate) [] | 37% | 37% | 37% | 37% | 35% | 39% |  |  |  | [1, 2, 3]
Cb coefficient (50°C/100°C)
Cv coefficient (50°C/100°C)
| Forced outage [] | ctrl: 0.9%; ctrl: 0.9%; ctrl: 0.9%; ctrl: 0.9%; -: 4
| Planned outage [weeks per year] | 0.17 | 0.17 | 0.17 | 0.17 |  |  |  |  | [D, E] | 5
| Technical lifetime [years] | ctrl: 25; ctrl: 25; ctrl: 25; ctrl: 25
| Construction time [years] | ctrl: 1; ctrl: 1; ctrl: 1; ctrl: 1; -: 6
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 100% | 100% | 100% | 100% |  |  |  |  | F | 6
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% |  |  |  |  | F | 6
Minimum load (of full load) [] | bar: ctrl to ctrl; -
| Warm start-up time [hours] | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.03 |  |  | H | [6, 7]
| Cold start-up time [hours] | 0.09 | 0.09 | 0.09 | 0.09 | 0.05 | 0.17 |  |  | H | 6
Environment
| SO2 [g/GJ_i] | 23 | 23 | 23 | 23 |  |  |  |  | I | 8
| NOX [g/GJ_i] | ctrl: 942; ctrl: 942; ctrl: 942; ctrl: 942; -: 8
| CH4 [g/GJ_i] | ctrl: 24; ctrl: 24; ctrl: 24; ctrl: 24; -: 8
| N2O [g/GJ_i] | ctrl: 2.1; ctrl: 2.1; ctrl: 2.1; ctrl: 2.1; -: 8
| Particles [g/GJ_i] | ctrl: 5; ctrl: 5; ctrl: 5; ctrl: 5; -: 8
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.37218 | 0.36155 | 0.36155 | 0.36155 | 0.28711 | 0.43598 | 0.25521 | 0.46788 | [M, N, O] | [1, 6, 9, 10]
| Nominal investment (equipment) [MEUR/MW_e] | 0.24458 | 0.23394 | 0.23394 | 0.23394 | 0 | 0 | 0 | 0 | L
| Nominal investment (installation) [MEUR/MW_e] | 0.1276 | 0.1276 | 0.1276 | 0.1276 | 0 | 0 | 0 | 0 | L
| Variable O&M (*total) [EUR/MWh_e] | 6.3802 | 6.3802 | 6.3802 | 6.3802 | 2.7648 | 9.0387 | 2.7648 | 9.0387 | 0 | [11, 12, 13]
| Fixed O&M (*total) [EUR/MW_e/y] | 9357.6799 | 9357.6799 | 8983.3727 | 8609.0655 | 0 | 0 | 0 | 0 | [D, P, Q] | 6
| Startup cost [EUR/MW_e/startup] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | R | [6, 11]
Technology-specific data
Notes:
A. The range of generating capacity for a plant based on this technology is tipically 10-300 MW. Most of UK projects are in the range 18.5-20 MW. Emission requirements for plants with 18.5 MW and above are regulated by the Danish EPA and it is as of yet undetermined whether and exemption due to low operating hours can be obtained.
B. Engine size is normally in the range 400 kW - 2 MW. Here considered 10 engines of 1.8 MW.
C. Assuming the same efficiency reduction from nameplate to annual average compared to Gas Engines in the main technology catalogue.
D. The routine checks and oil change varies depending on the size. Smaller engines (400 kW) needs it every 250 h, while larger engines (2 MW) needs it every 1000h. Here assumed larger engines. Fixed O&M costs can increase for smaller sizes.
E. 1.5h monthly maintenance for general checks, 4h semiannual, 2h annually, 2h biannually, 6h every 6 years.
F. 50% of the output capacity can be reach within 15 seconds and after 20 seconds the total power output can be provided.
G. Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level.
H. The startup time of the single engine is around 30 seconds. The syncronization of all the machines and the connection to the grid might increase the startup time to 3-10 minutes.
I. Values related to the use of gas oil.
L. Split based on the Engine technology in the main technology catalogue
M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N. The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.282-0.456 MEUR/MW.
O. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
Q. Assumed two times the reported value for service agreement excluding consumables, to take into account other fixed O&M components.
R. The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Interview with Rolls Royce Power Systems
2. C. Breyer. Fuel-Parity: New very large and sustainable market segments for PV systems. 2010
3. National Grid. Short Term Operating Reserve - Carbon intensity report. 2016
4. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
5. Maintenance schedule Caterpillar Emergency generator. Available at: https://ae.usembassy.gov/wp-content/uploads/sites/254/2017/06/stc12017q0002_post-provided-generator-checklist.pdf
6. Interview with UK manufacturer: Edina Power UK
7. Warstsila. White paper - Combustion engine power plants. 2011
8. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
9. Timera Energy. Investment in UK peaking assets. Available at: www.timera-energy.com/investment-in-uk-peaking-assets
10. UK Department for Business, Energy and Industrial Strategy. Electricity Generation Cost. November 2016
11. EUGINE (European Engine Power Plants Association) questionnaire to their members. Data presented in "Flexibility Needs and Options for Europe's Future Electricity System", Energy Brainpool, September 2017.
12. BEIS. Electricity Generation cost. November 2016
13. LAZARD. Levelized cost of energy analysis v11. November 2017

## 51 Natural gas engine plant
Technology |  | Engine, peak plant - back pressure - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 200; ctrl: 200; ctrl: 200; ctrl: 200; -: [A, B]
| Electrical efficiency (net, annual average) [] | 46% | 46% | 48% | 48% |  |  |  |  | D | 2
| Electrical efficiency (net, name plate) [] | 48% | 48% | 50% | 50% |  |  |  |  | C | 1
Cb coefficient (50°C/100°C)
Cv coefficient (50°C/100°C)
| Forced outage [] | ctrl: 0.9%; ctrl: 0.9%; ctrl: 0.9%; ctrl: 0.9%; -: 3
| Planned outage [weeks per year] | ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; -: E
| Technical lifetime [years] | ctrl: 25; ctrl: 25; ctrl: 25; ctrl: 25; -: F
| Construction time [years] | ctrl: 1; ctrl: 1; ctrl: 1; ctrl: 1; -: [4, 5]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 60% | 60% | 60% | 60% |  |  |  |  | G | 6
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% |  |  |  |  | G | 6
| Minimum load (of full load) [] | 1.5% | 1.5% | 1.5% | 1.5% |  |  |  |  | H | [6, 7]
| Warm start-up time [hours] | 0.03 | 0.03 | 0.03 | 0.03 |  |  |  |  | I | 7
| Cold start-up time [hours] | 0.17 | 0.17 | 0.17 | 0.17 |  |  |  |  | I | 7
Environment
| SO2 [g/GJ_i] | 0 | 0 | 0 | 0 |  |  |  |  | F | 2
| NOX [g/GJ_i] | 75 | 75 | 75 | 75 |  |  |  |  | F | 2
| CH4 [g/GJ_i] | 315 | 315 | 315 | 315 |  |  |  |  | F | 2
| N2O [g/GJ_i] | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | F | 2
| Particles [g/GJ_i] | ctrl: 0.76; ctrl: 0.76; ctrl: 0.76; ctrl: 0.76; -: 8
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.54232 | 0.52105 | 0.49979 | 0.47852 | 0.42535 | 0.62739 | 0.32965 | 0.61676 | [L, M, N, R] | [7, 5, 9]
| Nominal investment (equipment) [MEUR/MW_e] | 0.35091 | 0.34028 | 0.32965 | 0.30838 | 0 | 0 | 0 | 0 | F | 2
| Nominal investment (installation) [MEUR/MW_e] | 0.19141 | 0.18077 | 0.18077 | 0.17014 | 0 | 0 | 0 | 0 | F | 2
| Variable O&M (*total) [EUR/MWh_e] | 6.3802 | 6.3802 | 6.3802 | 6.3802 | 2.7648 | 9.0387 | 2.7648 | 9.0387 | 0 | [10, 11, 12]
| Fixed O&M (*total) [EUR/MW_e/y] | 6911.9227 | 6911.9227 | 6646.0795 | 6380.2363 | 0 | 0 | 0 | 0 | [O, P] | 7
| Startup cost [EUR/MW_e/startup] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Q | 10
Technology-specific data
Notes:
A. The technology is modular, normally composed by a certain amount of 2-10 MW engines. Here 20 engines of 10 MW are considered.
B. Typical capacity for ultra peakers and emergency plants is in the range 20-300 MW
C. Based on large gas motor (Wartsila 34SG)
D. Assuming the same efficiency reduction from nameplate to annual average compared to main technology catalogue.
E. Based on maintenance schedule of gas engines, considering the reduced number of operating hours and the fact that a typical scheduled maintenance services occurs after 2000, 4000 and 6000 hours, with 1 or 2 days of downtime each. No major maintenance window (16,000 h) is reached.
F. Based on the Gas Engine in the main technology catalogue
G. The values refers to the engine at nominal operating temperature.
H. Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level. Calculation done assuming 20x10MW engines.
I. The engines can startup from warm in 2 minutes. The plant cold startup time is affected by the need to warm up the transformers, which brings it up to 10 minutes. If engines and transformers are hot, the startup time is lower. In case of smaller plants connected to distribution grid, the time to warm up the transformer might not constitute a bottleneck.
L. Dual fuel operation can be considered. Impacting 3-4% of the total plant cost and 7% of engine cost
M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N. The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.443-0.616 MEUR/MW. The lower bound refers to smaller plants with smaller engines, while the higher bound refers to dual fuel plant, located further away from the grid.
O. The fixed O&M cost is lower than a typical value for plants operating >4000 h a year. A typical large maintenance window including reinvestment is carried after 10,000 running hours. Due to the low utilization, this type of plants might never need it in its lifetime, reducing the fixed O&M cost drastically. Additionally the central and lower estimates assume unmanned/remote operation of the plant, whereas the upper boundary assumes manned operation.
P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
Q. The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact. Modern technology can sustain up to 1000 cycles/years with no significant wear.
R. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Wartsila. Power Plant solutions 2016
2. Main technology catalogue: Technology Data for Energy Plants - August 2016
3. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
4. Kiisa Power plant project for Elering
5. Warstsila. White paper - Combustion engine power plants. 2011
6. D. Santoianni. Defining true flexibility - a comparison of gas-fired power generating technologies. 2015
7. Phone interview with Wartsila
8. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
9. UK Department for Business, Energy and Industrial Strategy. Electricity Generation Cost. November 2016
10. EUGINE (European Engine Power Plants Association) questionnaire to their members. Data presented in "Flexibility Needs and Options for Europe's Future Electricity System", Energy Brainpool, September 2017.
11. BEIS. Electricity Generation cost. November 2016
12. LAZARD. Levelized cost of energy analysis v11. November 2017

## 52 OCGT - Natural gas
Technology |  | Gas turbine, open cycle - back pressure - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 100; ctrl: 100; ctrl: 100; ctrl: 100; -: A
| Electrical efficiency (net, annual average) [] | 39% | 40% | 41% | 43% |  |  |  |  | C | 3
| Electrical efficiency (net, name plate) [] | 41% | 42% | 43% | 45% |  |  |  |  | [B, C] | [1, 2]
Cb coefficient (50°C/100°C)
Cv coefficient (50°C/100°C)
| Forced outage [] | ctrl: 1.37%; ctrl: 1.37%; ctrl: 1.37%; ctrl: 1.37%; -: 4
| Planned outage [weeks per year] | 0.11 | 0.11 | 0.11 | 0.11 |  |  |  |  | D | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 |  |  |  |  | E | 3
| Construction time [years] | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | F | 5
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 30% | 30% | 30% | 30% |  |  |  |  | G | 5
| Secondary regulation (of full load, per minute) [] | 30% | 30% | 30% | 30% | 15% | 50% |  |  | H | [5, 6, 7]
| Minimum load (of full load) [] | 25% | 20% | 20% | 20% |  |  |  |  | I | 8
| Warm start-up time [hours] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.11 |  |  |  | [8, 9, 10]
| Cold start-up time [hours] | 0.17 | 0.17 | 0.17 | 0.17 | 0.12 | 0.19 |  |  | L | [1, 6, 8]
Environment
| SO2 [g/GJ_i] | ctrl: 0.43; ctrl: 0.43; ctrl: 0.43; ctrl: 0.43; -: 11
| NOX [g/GJ_i] | ctrl: 48; ctrl: 48; ctrl: 48; ctrl: 48; -: 11
| CH4 [g/GJ_i] | ctrl: 1.7; ctrl: 1.7; ctrl: 1.7; ctrl: 1.7; -: 11
| N2O [g/GJ_i] | ctrl: 1; ctrl: 1; ctrl: 1; ctrl: 1; -: 11
| Particles [g/GJ_i] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; -: 11
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.49979 | 0.47852 | 0.46788 | 0.43598 | 0.38281 | 0.57422 | 0.30838 | 0.57422 | [M, N, O] | [7, 9, 10]
| Nominal investment (equipment) [MEUR/MW_e] | 0.39345 | 0.37218 | 0.36155 | 0.34028 | 0 | 0 | 0 | 0 | 0 | 12
| Nominal investment (installation) [MEUR/MW_e] | 0.10634 | 0.10634 | 0.10634 | 0.095704 | 0 | 0 | 0 | 0 | 0 | 12
| Variable O&M (*total) [EUR/MWh_e] | 4.7852 | 4.7852 | 4.7852 | 4.7852 | 3.7218 | 5.3169 | 3.7218 | 5.3169 | 0 | [5, 9, 10]
| Fixed O&M (*total) [EUR/MW_e/y] | 8579.2911 | 8579.2911 | 8236.1194 | 7892.9478 | 0 | 0 | 0 | 0 | P | 9
| Startup cost [EUR/MW_e/startup] | 45.725 | 45.725 | 45.725 | 45.725 | 0 | 0 | 0 | 0 | 0 | 9
Technology-specific data
Notes:
A. The range of generating capacity for a power plant based on this technology is tipically 50-200 MW. Large aeroderivative gas turbines have a rating of 20-100 MW.
B. The efficiency is drastically reduced at part-load. The difference between efficiency at full load and part load is on average 15%.
C. Based on the Simple Cycle Turbine in the main technology catalogue. No improvement assumed in the future
D. Considering one service per year for borescope inspection (18h). No major maintenance intervals reached, due to low utilization.
E. Lifetime most likely >25years, given low utilization
F. Some manufacturers offers pre-assembled mobile packages with installation in 30 days.
G. Based on a droop control of 0.65 MW/s of a Industrial Trent 60 (66MW) turbine at self-sustained speed.
H. Based on a gas turbine at self-sustained speed. Ramp rates of 15 MW/min to 50 MW/min.
I. The minimum emissions-compliant load is around 50%, but in case emission regulations do not apply, this can be lower. The efficiency is reduced at part-load (roughly 15%)
L. The lower bound of 7 minutes might be increased to 10 minutes if the plant is connected to high voltage and transformer needs to warm up before starting operations, similarly to Natural gas engine plants.
M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N. The specific investment cost can vary depending on a number of parameters, like size of turbine, electrical equipment and other characteristics. The specific investment in 2015 from several projects is in the range 0.400-0.570.
O. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. GE - Aeroderivative turbines product brochures.
2. Siemens - Aeroderivative turbine brochures
3. Main technology catalogue: Technology Data for Energy Plants - August 2016
4. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
5. M. Welch, T.Krol. Flexible Power Generation for Grid Support utilizing Aero-derivative Gas Turbine Technology. 2016
6. EU Turbines. Gas and Steam Turbines Solutions for a sustainable energy mix (brochure). 2017
7. Forrsa Power plant for Fingrid. Available at: www.fingrid.fi/en/pages/news/news/2013/fingrids-new-reserve-power-plant-inaugurated-in-forssa/
8. Agora Energiwende. Flexibility in thermal power plants. 2017
9. Energy Brainpool. Flexibility Needs and Options for Europe's Future Electricity System. September 2017.
10. Phone interview with Siemens Turbomachinery UK
11. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
12. ESMAP. Technical paper: Study of Equipment Prices in the Power Sector. 2009

## 52 OCGT - Light fuel oil
Technology |  | Gas turbine, open cycle - back pressure - light fuel oil - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
Generating capacity for one unit [MW_e]
| Electrical efficiency (net, annual average) [] | 38% | 39% | 40% | 42% | 38.5% | 40% |  |  | A | 18
| Electrical efficiency (net, name plate) [] | 4% | 41% | 42% | 44% | 40.5% | 42% |  |  | A | 18
Cb coefficient (50°C/100°C)
Cv coefficient (50°C/100°C)
Forced outage []
Planned outage [weeks per year]
Technical lifetime [years]
Construction time [years]
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) []
| Warm start-up time [hours] | 0.09 | 0.09 | 0.09 | 0.09 |  |  |  |  | A | 18
| Cold start-up time [hours] | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | A | 18
Environment
| SO2 [g/GJ_i] | 23 | 23 | 23 | 23 |  |  |  |  | B | 11
| NOX [g/GJ_i] | 230 | 230 | 230 | 230 |  |  |  |  | B | 11
| CH4 [g/GJ_i] | 3 | 3 | 3 | 3 |  |  |  |  | B | 11
| N2O [g/GJ_i] | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | B | 11
| Particles [g/GJ_i] | 5 | 5 | 5 | 5 |  |  |  |  | B | 11
Financial data
| Nominal investment (*total) [MEUR/MW_e] | 0.41472 | 0.40408 | 0.38281 | 0.36155 | 0.31901 | 0.47852 | 0.25521 | 0.47852 | [C, D] | 19
| Nominal investment (equipment) [MEUR/MW_e] | 0.31901 | 0.31901 | 0.29774 | 0.28711 | 0 | 0 | 0 | 0 | 0 | 20
| Nominal investment (installation) [MEUR/MW_e] | 0.095704 | 0.08507 | 0.08507 | 0.08507 | 0 | 0 | 0 | 0 | 0 | 20
| Variable O&M (*total) [EUR/MWh_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [EUR/MW_e/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Startup cost [EUR/MW_e/startup] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
Notes:
A. Value indicate the estimated change from the correspondent value of natural gas fuelled plant (unit is the same as the paramter).
B. Emission values for Gas Oil. If Residual Oil used, SO2 emissions increased to 100g, NOx reduced to 138g and Particles to 3g.
C. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016. Same development as natural gas fuelled plant, since the technology is the same.
D. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
11. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
18. Phone interview with Siemens Turbomachinery UK
19. Forrsa Power plant for Fingrid. Available at: www.fingrid.fi/en/pages/news/news/2013/fingrids-new-reserve-power-plant-inaugurated-in-forssa/
20. ESMAP. Technical paper: Study of Equipment Prices in the Power Sector. 2009